## techniques
ID | name | description | url | created | last modified | contributors | tactics | platforms | data sources
T0800 | Activate Firmware Update Mode | Adversaries may activate firmware update mode on devices to prevent expected response functions from engaging in reaction to an emergency or process malfunction. For example, devices such as protection relays may have an operation mode designed for firmware installation. This mode may halt process monitoring and related functions to allow new firmware to be loaded. A device left in update mode may be placed in an inactive holding state if no firmware is provided to it. By entering and leaving a device in this mode, the adversary may deny its usual functionalities. | https://collaborate.mitre.org/attackics/index.php/Technique/T0800 | 21 May 2020 | 08 October 2021 | Joe Slowik - Dragos | Inhibit Response Function | Field Controller/RTU/PLC/IED, Safety Instrumented System/Protection Relay | Application Log: Application Log Content, Network Traffic: Network Traffic Content, Operational Databases: Device Alarm
T0878 | Alarm Suppression | Adversaries may target protection function alarms to prevent them from notifying operators of critical conditions. Alarm messages may be a part of an overall reporting system and of particular interest for adversaries. Disruption of the alarm system does not imply the disruption of the reporting system as a whole. In the Maroochy Attack, the adversary suppressed alarm reporting to the central computer. (Citation: Maroochy - MITRE - 200808) A Secura presentation on targeting OT notes a dual fold goal for adversaries attempting alarm suppression: prevent outgoing alarms from being raised and prevent incoming alarms from being responded to. (Citation: References - Secura - 2019) The method of suppression may greatly depend on the type of alarm in question: * An alarm raised by a protocol message * An alarm signaled with I/O * An alarm bit set in a flag (and read) In ICS environments, the adversary may have to suppress or contend with multiple alarms and/or alarm propagation to achieve a specific goal to evade detection or prevent intended responses from occurring. (Citation: References - Secura - 2019) Methods of suppression may involve tampering or altering device displays and logs, modifying in memory code to fixed values, or even tampering with assembly level instruction code. | https://collaborate.mitre.org/attackics/index.php/Technique/T0878 | 21 May 2020 | 08 October 2021 | Jos Wetzels - Midnight Blue; Marina Krotofil | Inhibit Response Function | Device Configuration/Parameters, Field Controller/RTU/PLC/IED, Safety Instrumented System/Protection Relay | Application Log: Application Log Content, Network Traffic: Network Traffic Content, Operational Databases: Process History/Live Data, Operational Databases: Process/Event Alarm
T0802 | Automated Collection | Adversaries may automate collection of industrial environment information using tools or scripts. This automated collection may leverage native control protocols and tools available in the control systems environment. For example, the OPC protocol may be used to enumerate and gather information. Access to a system or interface with these native protocols may allow collection and enumeration of other attached, communicating servers and devices. | https://collaborate.mitre.org/attackics/index.php/Technique/T0802 | 21 May 2020 | 08 October 2021 |  | Collection Ics | Control Server, Field Controller/RTU/PLC/IED, Safety Instrumented System/Protection Relay | Command: Command Execution, File: File Access, Network Traffic: Network Traffic Content, Script: Script Execution
T0803 | Block Command Message | Adversaries may block a command message from reaching its intended target to prevent command execution. In OT networks, command messages are sent to provide instructions to control system devices. A blocked command message can inhibit response functions from correcting a disruption or unsafe condition.(Citation: Research - Research - Taxonomy Cyber Attacks on SCADA)(Citation: Ukraine15 - EISAC - 201603) | https://collaborate.mitre.org/attackics/index.php/Technique/T0803 | 21 May 2020 | 08 October 2021 |  | Inhibit Response Function | Device Configuration/Parameters, Field Controller/RTU/PLC/IED | Application Log: Application Log Content, Network Traffic: Network Connection Creation, Network Traffic: Network Traffic Flow, Operational Databases: Process History/Live Data, Operational Databases: Process/Event Alarm, Process: Process Termination
T0804 | Block Reporting Message | Adversaries may block or prevent a reporting message from reaching its intended target. In control systems, reporting messages contain telemetry data (e.g., I/O values) pertaining to the current state of equipment and the industrial process. By blocking these reporting messages, an adversary can potentially hide their actions from an operator. Blocking reporting messages in control systems that manage physical processes may contribute to system impact, causing inhibition of a response function. A control system may not be able to respond in a proper or timely manner to an event, such as a dangerous fault, if its corresponding reporting message is blocked.(Citation: Research - Research - Taxonomy Cyber Attacks on SCADA)(Citation: Ukraine15 - EISAC - 201603) | https://collaborate.mitre.org/attackics/index.php/Technique/T0804 | 21 May 2020 | 08 October 2021 |  | Inhibit Response Function | Device Configuration/Parameters, Field Controller/RTU/PLC/IED, Input/Output Server | Application Log: Application Log Content, Network Traffic: Network Connection Creation, Network Traffic: Network Traffic Flow, Operational Databases: Process History/Live Data, Operational Databases: Process/Event Alarm, Process: Process Termination
T0805 | Block Serial COM | Adversaries may block access to serial COM to prevent instructions or configurations from reaching target devices. Serial Communication ports (COM) allow communication with control system devices. Devices can receive command and configuration messages over such serial COM. Devices also use serial COM to send command and reporting messages. Blocking device serial COM may also block command messages and block reporting messages. A serial to Ethernet converter is often connected to a serial COM to facilitate communication between serial and Ethernet devices. One approach to blocking a serial COM would be to create and hold open a TCP session with the Ethernet side of the converter. A serial to Ethernet converter may have a few ports open to facilitate multiple communications. For example, if there are three serial COM available -- 1, 2 and 3 --, the converter might be listening on the corresponding ports 20001, 20002, and 20003. If a TCP/IP connection is opened with one of these ports and held open, then the port will be unavailable for use by another party. One way the adversary could achieve this would be to initiate a TCP session with the serial to Ethernet converter at <code>10.0.0.1</code> via Telnet on serial port 1 with the following command: <code>telnet 10.0.0.1 20001</code>. | https://collaborate.mitre.org/attackics/index.php/Technique/T0805 | 21 May 2020 | 08 October 2021 |  | Inhibit Response Function | Device Configuration/Parameters, Field Controller/RTU/PLC/IED, Input/Output Server | Application Log: Application Log Content, Network Traffic: Network Connection Creation, Network Traffic: Network Traffic Flow, Operational Databases: Process History/Live Data, Operational Databases: Process/Event Alarm, Process: Process Termination
T0806 | Brute Force I/O | Adversaries may repetitively or successively change I/O point values to perform an action. Brute Force I/O may be achieved by changing either a range of I/O point values or a single point value repeatedly to manipulate a process function. The adversary’s goal and the information they have about the target environment will influence which of the options they choose. In the case of brute forcing a range of point values, the adversary may be able to achieve an impact without targeting a specific point. In the case where a single point is targeted, the adversary may be able to generate instability on the process function associated with that particular point. Adversaries may use Brute Force I/O to cause failures within various industrial processes. These failures could be the result of wear on equipment, or damage to downstream equipment. | https://collaborate.mitre.org/attackics/index.php/Technique/T0806 | 21 May 2020 | 14 October 2021 |  | Impair Process Control | Control Server, Field Controller/RTU/PLC/IED | Application Log: Application Log Content, Network Traffic: Network Traffic Content, Operational Databases: Process History/Live Data
T0858 | Change Operating Mode | Adversaries Adversaries may change the operating mode of a controller to gain additional access to engineering functions such as Program Download. Programmable controllers typically have several modes of operation that control the state of the user program and control access to the controller’s API. Operating modes can be physically selected using a key switch on the face of the controller but may also be selected with calls to the controller’s API. Operating modes and the mechanisms by which they are selected often vary by vendor and product line. Some commonly implemented operating modes are described below: Program - This mode must be enabled before changes can be made to a device’s program. This allows program uploads and downloads between the device and an engineering workstation. Often the PLC’s logic Is halted, and all outputs may be forced off.(Citation: Forum Automation PLC Operating Modes October 2017) Run - Execution of the device’s program occurs in this mode. Input and output (values, points, tags, elements, etc.) are monitored and used according to the program’s logic. Program Upload and Program Download are disabled while in this mode.(Citation: Omrom PLC Different Operating Modes)(Citation: Machine Information Systems How PLCs Work 2007)(Citation: Forum Automation PLC Operating Modes October 2017)(Citation: PLCgurus PLC Basics 2021) Remote - Allows for remote changes to a PLC’s operation mode.(Citation: PLCgurus PLC Basics 2021) Stop - The PLC and program is stopped, while in this mode, outputs are forced off.(Citation: Machine Information Systems How PLCs Work 2007) Reset - Conditions on the PLC are reset to their original states. Warm resets may retain some memory while cold resets will reset all I/O and data registers.(Citation: Machine Information Systems How PLCs Work 2007)Test / Monitor mode - Similar to run mode, I/O is processed, although this mode allows for monitoring, force set, resets, and more generally tuning or debugging of the system. Often monitor mode may be used as a trial for initialization.(Citation: Omrom PLC Different Operating Modes) | https://collaborate.mitre.org/attackics/index.php/Technique/T0858 | 21 May 2020 | 08 October 2021 |  | Evasion Ics, Execution Ics | Field Controller/RTU/PLC/IED, Safety Instrumented System/Protection Relay | Application Log: Application Log Content, Network Traffic: Network Traffic Content, Operational Databases: Device Alarm
T0807 | Command-Line Interface | Adversaries may utilize command-line interfaces (CLIs) to interact with systems and execute commands. CLIs provide a means of interacting with computer systems and are a common feature across many types of platforms and devices within control systems environments. (Citation: EAttack Command-Line Interface) Adversaries may also use CLIs to install and run new software, including malicious tools that may be installed over the course of an operation. CLIs are typically accessed locally, but can also be exposed via services, such as SSH, Telnet, and RDP. Commands that are executed in the CLI execute with the current permissions level of the process running the terminal emulator, unless the command specifies a change in permissions context. Many controllers have CLI interfaces for management purposes. Detection: Command-line interface activities can be captured through proper logging of process execution with command-line arguments. This information can be useful in gaining additional insight to adversaries' actions through how they use native processes or custom tools. | https://collaborate.mitre.org/attackics/index.php/Technique/T0807 | 21 May 2020 | 08 October 2021 |  | Execution Ics | Control Server, Data Historian, Field Controller/RTU/PLC/IED, Human-Machine Interface, Input/Output Server | Command: Command Execution, Module: Module Load, Process: Process Creation, Process: Process Creation, Script: Script Execution
T0885 | Commonly Used Port | Adversaries may communicate over a commonly used port to bypass firewalls or network detection systems and to blend in with normal network activity, to avoid more detailed inspection. They may use the protocol associated with the port, or a completely different protocol. They may use commonly open ports, such as the examples provided below. * TCP:80 (HTTP) * TCP:443 (HTTPS) * TCP/UDP:53 (DNS) * TCP:1024-4999 (OPC on XP/Win2k3) * TCP:49152-65535 (OPC on Vista and later) * TCP:23 (TELNET) * UDP:161 (SNMP) * TCP:502 (MODBUS) * TCP:102 (S7comm/ISO-TSAP) * TCP:20000 (DNP3) * TCP:44818 (Ethernet/IP) Contributors: Matan Dobrushin - Otorio | https://collaborate.mitre.org/attackics/index.php/Technique/T0885 | 21 May 2020 | 08 October 2021 | Matan Dobrushin - Otorio | Command And Control Ics | Control Server, Engineering Workstation, Field Controller/RTU/PLC/IED, Human-Machine Interface, Safety Instrumented System/Protection Relay | Network Traffic: Network Traffic Flow
T0884 | Connection Proxy | Adversaries may use a connection proxy to direct network traffic between systems or act as an intermediary for network communications. The definition of a proxy can also be expanded to encompass trust relationships between networks in peer-to-peer, mesh, or trusted connections between networks consisting of hosts or systems that regularly communicate with each other. The network may be within a single organization or across multiple organizations with trust relationships. Adversaries could use these types of relationships to manage command and control communications, to reduce the number of simultaneous outbound network connections, to provide resiliency in the face of connection loss, or to ride over existing trusted communications paths between victims to avoid suspicion. (Citation: EAttack Connection Proxy) Detection: Processes utilizing the network that do not normally have network communication or have never been seen before are suspicious. Network activities disassociated from user-driven actions from processes that normally require user direction are suspicious. Analyze network data for uncommon data flows (e.g., a client sending significantly more data than it receives from a server or between clients that should not or often do not communicate with one another). Processes utilizing the network that do not normally have network communication or have never been seen before are suspicious. Analyze packet contents to detect communications that do not follow the expected protocol behavior for the port that is being used. (Citation: University of Birmingham C2) | https://collaborate.mitre.org/attackics/index.php/Technique/T0884 | 21 May 2020 | 08 October 2021 |  | Command And Control Ics | None | Network Traffic: Network Connection Creation, Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow
T0879 | Damage to Property | Adversaries may cause damage and destruction of property to infrastructure, equipment, and the surrounding environment when attacking control systems. This technique may result in device and operational equipment breakdown, or represent tangential damage from other techniques used in an attack. Depending on the severity of physical damage and disruption caused to control processes and systems, this technique may result in <span class="smw-format list-format "><span class="smw-row"><span class="smw-field"><span class="smw-value">Loss of Safety</span></span></span></span>. Operations that result in <span class="smw-format list-format "><span class="smw-row"><span class="smw-field"><span class="smw-value">Loss of Control</span></span></span></span> may also cause damage to property, which may be directly or indirectly motivated by an adversary seeking to cause impact in the form of <span class="smw-format list-format "><span class="smw-row"><span class="smw-field"><span class="smw-value">Loss of Productivity and Revenue</span></span></span></span>. The German Federal Office for Information Security (BSI) reported a targeted attack on a steel mill under an incidents affecting business section of its 2014 IT Security Report. (Citation: German Steel Mill - German Federal Office for Information Security - 2014) These targeted attacks affected industrial operations and resulted in breakdowns of control system components and even entire installations. As a result of these breakdowns, massive impact and damage resulted from the uncontrolled shutdown of a blast furnace. In the Maroochy Attack, Vitek Boden gained remote computer access to the control system and altered data so that whatever function should have occurred at affected pumping stations did not occur or occurred in a different way. This ultimately led to 800,000 liters of raw sewage being spilled out into the community. The raw sewage affected local parks, rivers, and even a local hotel. This resulted in harm to marine life and produced a sickening stench from the community's now blackened rivers. (Citation: Maroochy - MITRE - 200808) A Polish student used a remote controller device to interface with the Lodz city tram system in Poland. (Citation: LodzTram-LondonReconnections-2017-12) (Citation: LodzTram-InHomelandSecurity-2008-02) (Citation: LodzTram-Schneier-2008-01) Using this remote, the student was able to capture and replay legitimate tram signals. This resulted in damage to impacted trams, people, and the surrounding property. Reportedly, four trams were derailed and were forced to make emergency stops. (Citation: LodzTram-InHomelandSecurity-2008-02) Commands issued by the student may have also resulted in tram collisions, causing harm to those on board and the environment outside. (Citation: LodzTram-Schneier-2008-01) | https://collaborate.mitre.org/attackics/index.php/Technique/T0879 | 21 May 2020 | 08 October 2021 |  | Impact Ics | None
T0809 | Data Destruction | Adversaries may perform data destruction over the course of an operation. The adversary may drop or create malware, tools, or other non-native files on a target system to accomplish this, potentially leaving behind traces of malicious activities. Such non-native files and other data may be removed over the course of an intrusion to maintain a small footprint or as a standard part of the post-intrusion cleanup process. (Citation: EAttack File Deletion) Data destruction may also be used to render operator interfaces unable to respond and to disrupt response functions from occurring as expected. An adversary may also destroy data backups that are vital to recovery after an incident. Standard file deletion commands are available on most operating system and device interfaces to perform cleanup, but adversaries may use other tools as well. Two examples are Windows Sysinternals SDelete and Active@ Killdisk. Detection: It may be uncommon for events related to benign command-line functions such as DEL or third-party utilities or tools to be found in an environment, depending on the user base and how systems are typically used. Monitoring for command-line deletion functions to correlate with binaries or other files that an adversary may drop and remove may lead to detection of malicious activity. Another good practice is monitoring for known deletion and secure deletion tools that are not already on systems within an enterprise network that an adversary could introduce. Some monitoring tools may collect command-line arguments, but may not capture DEL commands since DEL is a native function within cmd.exe. | https://collaborate.mitre.org/attackics/index.php/Technique/T0809 | 21 May 2020 | 08 October 2021 | Matan Dobrushin - Otorio | Inhibit Response Function | Control Server, Field Controller/RTU/PLC/IED, Human-Machine Interface | Command: Command Execution, File: File Deletion, File: File Modification, Process: Process Creation
T0811 | Data from Information Repositories | Adversaries may target and collect data from information repositories. This can include sensitive data such as specifications, schematics, or diagrams of control system layouts, devices, and processes. Examples of information repositories include reference databases or local machines in the process environment, as well as workstations and databases in the corporate network that might contain information about the ICS. Information collected from these systems may provide the adversary with a better understanding of the operational environment, vendors used, processes, or procedures of the ICS. In a campaign between 2011 and 2013 against ONG organizations, Chinese state-sponsored actors searched document repositories for specific information such as, system manuals, remote terminal unit (RTU) sites, personnel lists, documents that included the string “SCAD*”, user credentials, and remote dial-up access information.(Citation: CISA Chinese Gas Pipeline Intrusion 2011 - 2013 July 2021) | https://collaborate.mitre.org/attackics/index.php/Technique/T0811 | 21 May 2020 | 08 October 2021 |  | Collection Ics | Control Server, Data Historian, Engineering Workstation, Human-Machine Interface | Application Log: Application Log Content, File: File Access, Logon Session: Logon Session Creation
T0812 | Default Credentials | Adversaries may leverage manufacturer or supplier set default credentials on control system devices. These default credentials may have administrative permissions and may be necessary for initial configuration of the device. It is general best practice to change the passwords for these accounts as soon as possible, but some manufacturers may have devices that have passwords or usernames that cannot be changed. (Citation: Guidance - NIST SP800-82) Default credentials are normally documented in an instruction manual that is either packaged with the device, published online through official means, or published online through unofficial means. Adversaries may leverage default credentials that have not been properly modified or disabled. | https://collaborate.mitre.org/attackics/index.php/Technique/T0812 | 21 May 2020 | 08 October 2021 |  | Lateral Movement Ics | Control Server, Engineering Workstation, Field Controller/RTU/PLC/IED, Human-Machine Interface, Safety Instrumented System/Protection Relay | Logon Session: Logon Session Creation, Network Traffic: Network Traffic Content
T0813 | Denial of Control | Adversaries may cause a denial of control to temporarily prevent operators and engineers from interacting with process controls. An adversary may attempt to deny process control access to cause a temporary loss of communication with the control device or to prevent operator adjustment of process controls. An affected process may still be operating during the period of control loss, but not necessarily in a desired state. (Citation: Reference - Corero) (Citation: Reference - SANS - 201510) (Citation: Reference - RIoT) In the Maroochy attack, the adversary was able to temporarily shut an investigator out of the network preventing them from issuing any controls. In the 2017 Dallas Siren incident operators were unable to disable the false alarms from the Office of Emergency Management headquarters. | https://collaborate.mitre.org/attackics/index.php/Technique/T813 | 21 May 2020 | 21 April 2021 |  | Impact Ics | Windows
T0814 | Denial of Service | Adversaries may perform Denial-of-Service (DoS) attacks to disrupt expected device functionality. Examples of DoS attacks include overwhelming the target device with a high volume of requests in a short time period and sending the target device a request it does not know how to handle. Disrupting device state may temporarily render it unresponsive, possibly lasting until a reboot can occur. When placed in this state, devices may be unable to send and receive requests, and may not perform expected response functions in reaction to other events in the environment. Some ICS devices are particularly sensitive to DoS events, and may become unresponsive in reaction to even a simple ping sweep. Adversaries may also attempt to execute a Permanent Denial-of-Service (PDoS) against certain devices, such as in the case of the BrickerBot malware. (Citation: BrickerBot - ICS-CERT - Alert) Adversaries may exploit a software vulnerability to cause a denial of service by taking advantage of a programming error in a program, service, or within the operating system software or kernel itself to execute adversary-controlled code. Vulnerabilities may exist in software that can be used to cause a or denial of service condition. Adversaries may have prior knowledge about industrial protocols or control devices used in the environment through <span class="smw-format list-format "><span class="smw-row"><span class="smw-field"><span class="smw-value">Control Device Identification</span></span></span></span>. There are examples of adversaries remotely causing a <span class="smw-format list-format "><span class="smw-row"><span class="smw-field"><span class="smw-value">Device Restart/Shutdown</span></span></span></span> by exploiting a vulnerability that induces uncontrolled resource consumption. (Citation: Industroyer - ICS-CERT ADV) (Citation: Industroyer - CWE-400) (Citation: Industroyer - CVE-2015-5374) In the Maroochy attack, the adversary was able to shut an investigator out of the network. (Citation: Maroochy - MITRE - 200808) | https://collaborate.mitre.org/attackics/index.php/Technique/T0814 | 21 May 2020 | 08 October 2021 |  | Inhibit Response Function | Field Controller/RTU/PLC/IED, Safety Instrumented System/Protection Relay | Application Log: Application Log Content, Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow, Operational Databases: Process History/Live Data
T0815 | Denial of View | Adversaries may cause a denial of view in attempt to disrupt and prevent operator oversight on the status of an ICS environment. This may manifest itself as a temporary communication failure between a device and its control source, where the interface recovers and becomes available once the interference ceases. (Citation: Reference - Corero) (Citation: Reference - SANS - 201510) (Citation: Reference - RIoT) An adversary may attempt to deny operator visibility by preventing them from receiving status and reporting messages. Denying this view may temporarily block and prevent operators from noticing a change in state or anomalous behavior. The environment's data and processes may still be operational, but functioning in an unintended or adversarial manner. In the Maroochy attack, the adversary was able to temporarily shut an investigator out of the network, preventing them from viewing the state of the system. | https://collaborate.mitre.org/attackics/index.php/Technique/T0815 | 21 May 2020 | 21 May 2020 |  | Impact Ics | None
T0868 | Detect Operating Mode | Adversaries may gather information about a PLC’s or controller’s current operating mode. Operating modes dictate what change or maintenance functions can be manipulated and are often controlled by a key switch on the PLC (e.g., run, prog [program], and remote). Knowledge of these states may be valuable to an adversary to determine if they are able to reprogram the PLC. Operating modes and the mechanisms by which they are selected often vary by vendor and product line. Some commonly implemented operating modes are described below: Program - This mode must be enabled before changes can be made to a device’s program. This allows program uploads and downloads between the device and an engineering workstation. Often the PLC’s logic Is halted, and all outputs may be forced off. Run - Execution of the device’s program occurs in this mode. Input and output (values, points, tags, elements, etc.) are monitored and used according to the program’s logic. Program Upload and Program Download are disabled while in this mode. Remote - Allows for remote changes to a PLC’s operation mode. Stop - The PLC and program is stopped, while in this mode, outputs are forced off. Reset - Conditions on the PLC are reset to their original states. Warm resets may retain some memory while cold resets will reset all I/O and data registers. Test / Monitor mode - Similar to run mode, I/O is processed, although this mode allows for monitoring, force set, resets, and more generally tuning or debugging of the system. Often monitor mode may be used as a trial for initialization. | https://collaborate.mitre.org/attackics/index.php/Technique/T0868 | 21 May 2020 | 08 October 2021 |  | Collection Ics | Field Controller/RTU/PLC/IED | Network Traffic: Network Traffic Content
T0816 | Device Restart/Shutdown | Adversaries may forcibly restart or shutdown a device in an ICS environment to disrupt and potentially negatively impact physical processes. Methods of device restart and shutdown exist in some devices as built-in, standard functionalities. These functionalities can be executed using interactive device web interfaces, CLIs, and network protocol commands. Unexpected restart or shutdown of control system devices may prevent expected response functions happening during critical states. A device restart can also be a sign of malicious device modifications, as many updates require a shutdown in order to take effect. | https://collaborate.mitre.org/attackics/index.php/Technique/T0816 | 21 May 2020 | 08 October 2021 |  | Inhibit Response Function | Field Controller/RTU/PLC/IED | Application Log: Application Log Content, Network Traffic: Network Traffic Content, Operational Databases: Device Alarm
T0817 | Drive-by Compromise | Adversaries may gain access to a system during a drive-by compromise, when a user visits a website as part of a regular browsing session.With this technique, the user's web browser is targeted and exploited simply by visiting the compromised website. The adversary may target a specific community, such as trusted third party suppliers or other industry specific groups, which often visit the target website. This kind of targeted attack relies on a common interest, and is known as a strategic web compromise or watering hole attack. The National Cyber Awareness System (NCAS) has issued a Technical Alert (TA) regarding Russian government cyber activity targeting critical infrastructure sectors. (Citation: Alert - CISA TA18-074A) Analysis by DHS and FBI has noted two distinct categories of victims in the Dragonfly campaign on the Western energy sector: staging and intended targets. The adversary targeted the less secure networks of staging targets, including trusted third-party suppliers and related peripheral organizations. Initial access to the intended targets used watering hole attacks to target process control, ICS, and critical infrastructure related trade publications and informational websites. | https://collaborate.mitre.org/attackics/index.php/Technique/T0817 | 21 May 2020 | 08 October 2021 |  | Initial Access Ics | None | Application Log: Application Log Content, File: File Creation, Network Traffic: Network Traffic Content, Process: Process Creation
T0871 | Execution through API | Adversaries may attempt to leverage Application Program Interfaces (APIs) used for communication between control software and the hardware. Specific functionality is often coded into APIs which can be called by software to engage specific functions on a device or other software. | https://collaborate.mitre.org/attackics/index.php/Technique/T0871 | 21 May 2020 | 08 October 2021 |  | Execution Ics | Field Controller/RTU/PLC/IED | Module: Module Load, Network Traffic: Network Traffic Content
T0819 | Exploit Public-Facing Application | Adversaries may leverage weaknesses to exploit internet-facing software for initial access into an industrial network. Internet-facing software may be user applications, underlying networking implementations, an assets operating system, weak defenses, etc. Targets of this technique may be intentionally exposed for the purpose of remote management and visibility. An adversary may seek to target public-facing applications as they may provide direct access into an ICS environment or the ability to move into the ICS network. Publicly exposed applications may be found through online tools that scan the internet for open ports and services. Version numbers for the exposed application may provide adversaries an ability to target specific known vulnerabilities. Exposed control protocol or remote access ports found in Commonly Used Port may be of interest by adversaries. | https://collaborate.mitre.org/attackics/index.php/Technique/T0819 | 21 May 2020 | 08 October 2021 |  | Initial Access Ics | Human-Machine Interface | Application Log: Application Log Content, Network Traffic: Network Traffic Content
T0820 | Exploitation for Evasion | Adversaries may exploit a software vulnerability to take advantage of a programming error in a program, service, or within the operating system software or kernel itself to evade detection. Vulnerabilities may exist in software that can be used to disable or circumvent security features. Adversaries may have prior knowledge through <span class="smw-format list-format "><span class="smw-row"><span class="smw-field"><span class="smw-value">Control Device Identification</span></span></span></span> about security features implemented on control devices. These device security features will likely be targeted directly for exploitation. There are examples of firmware RAM/ROM consistency checks on control devices being targeted by adversaries to enable the installation of malicious System Firmware | https://collaborate.mitre.org/attackics/index.php/Technique/T0820 | 21 May 2020 | 08 October 2021 |  | Evasion Ics | Field Controller/RTU/PLC/IED, Safety Instrumented System/Protection Relay
T0890 | Exploitation for Privilege Escalation | Adversaries may exploit software vulnerabilities in an attempt to elevate privileges. Exploitation of a software vulnerability occurs when an adversary takes advantage of a programming error in a program, service, or within the operating system software or kernel itself to execute adversary-controlled code. Security constructs such as permission levels will often hinder access to information and use of certain techniques, so adversaries will likely need to perform privilege escalation to include use of software exploitation to circumvent those restrictions. When initially gaining access to a system, an adversary may be operating within a lower privileged process which will prevent them from accessing certain resources on the system. Vulnerabilities may exist, usually in operating system components and software commonly running at higher permissions, that can be exploited to gain higher levels of access on the system. This could enable someone to move from unprivileged or user level permissions to SYSTEM or root permissions depending on the component that is vulnerable. This may be a necessary step for an adversary compromising an endpoint system that has been properly configured and limits other privilege escalation methods. | https://collaborate.mitre.org/attackics/index.php/Technique/T0890 | 13 April 2021 | 08 October 2021 |  | Privilege Escalation Ics | Human-Machine Interface, Safety Instrumented System/Protection Relay | Process: OS API Execution
T0866 | Exploitation of Remote Services | Adversaries may exploit a software vulnerability to take advantage of a programming error in a program, service, or within the operating system software or kernel itself to enable remote service abuse. A common goal for post-compromise exploitation of remote services is for lateral movement to enable access to a remote system. (Citation: EAttack Exploitation of Remote Services) ICS asset owners and operators have been affected by ransomware (or disruptive malware masquerading as ransomware) migrating from enterprise IT to ICS environments: WannaCry, NotPetya, and BadRabbit. In each of these cases, self-propagating (“wormable”) malware initially infected IT networks, but through exploit (particularly the SMBv1-targeting MS17-010 vulnerability) spread to industrial networks, producing significant impacts. (Citation: Reference - Dragos - 201910) | https://collaborate.mitre.org/attackics/index.php/Technique/T0866 | 21 May 2020 | 08 October 2021 |  | Initial Access Ics, Lateral Movement Ics | Data Historian, Engineering Workstation, Human-Machine Interface | Application Log: Application Log Content, Network Traffic: Network Traffic Content
T0822 | External Remote Services | Adversaries may leverage external remote services as a point of initial access into your network. These services allow users to connect to internal network resources from external locations. Examples are VPNs, Citrix, and other access mechanisms. Remote service gateways often manage connections and credential authentication for these services.(Citation: EAttack External Remote Services) External remote services allow administration of a control system from outside the system. Often, vendors and internal engineering groups have access to external remote services to control system networks via the corporate network. In some cases, this access is enabled directly from the internet. While remote access enables ease of maintenance when a control system is in a remote area, compromise of remote access solutions is a liability. The adversary may use these services to gain access to and execute attacks against a control system network. Access to valid accounts is often a requirement. As they look for an entry point into the control system network, adversaries may begin searching for existing point‐to‐point VPN implementations at trusted third party networks or through remote support employee connections where split tunneling is enabled.(Citation: Ukraine15 - EISAC - 201603) In the Maroochy Attack, the adversary was able to gain remote computer access to the system over radio. | https://collaborate.mitre.org/attackics/index.php/Technique/T0822 | 21 May 2020 | 08 October 2021 |  | Initial Access Ics | Control Server, Input/Output Server | Application Log: Application Log Content, Logon Session: Logon Session Metadata, Network Traffic: Network Traffic Flow
T0823 | Graphical User Interface | Adversaries may attempt to gain access to a machine via a Graphical User Interface (GUI) to enhance execution capabilities. Access to a GUI allows a user to interact with a computer in a more visual manner than a CLI. A GUI allows users to move a cursor and click on interface objects, with a mouse and keyboard as the main input devices, as opposed to just using the keyboard. If physical access is not an option, then access might be possible via protocols such as VNC on Linux-based and Unix-based operating systems, and RDP on Windows operating systems. An adversary can use this access to execute programs and applications on the target machine. In the Oldsmar water treatment attack, adversaries utilized the operator HMI interface through the graphical user interface. This action led to immediate operator detection as they were able to see the adversary making changes on their screen. (Citation: Oldsmar Water Treatment Attack Feb 2021) | https://collaborate.mitre.org/attackics/index.php/Technique/T0823 | 21 May 2020 | 14 October 2021 |  | Execution Ics | Human-Machine Interface | Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow, Process: Process Creation
T0874 | Hooking | Adversaries may hook into application programming interface (API) functions used by processes to redirect calls for persistent means. Windows processes often leverage these API functions to perform tasks that require reusable system resources. Windows API functions are typically stored in dynamic-link libraries (DLLs) as exported functions. (Citation: EAttack Hooking) One type of hooking seen in ICS involves redirecting calls to these functions via import address table (IAT) hooking. IAT hooking uses modifications to a process’s IAT, where pointers to imported API functions are stored. (Citation: Stuxnet - Symantec - 201102) | https://collaborate.mitre.org/attackics/index.php/Technique/T0874 | 21 May 2020 | 08 October 2021 |  | Execution Ics, Privilege Escalation Ics | Engineering Workstation | File: File Modification, Module: Module Load
T0877 | I/O Image | Adversaries may seek to capture process image values related to the inputs and outputs of a PLC. Within a PLC all input and output states are stored into an I/O image. This image is used by the user program instead of directly interacting with physical I/O. (Citation: PLC-Blaster 2) Adversaries may collect the I/O Image state of a PLC by utilizing a device’s Native API to access the memory regions directly. The collection of the PLC’s I/O state could be used to replace values or inform future stages of an attack. | https://collaborate.mitre.org/attackics/index.php/Technique/T0877 | 21 May 2020 | 14 October 2021 |  | Collection Ics | Field Controller/RTU/PLC/IED | Asset: Software/Firmware
T0872 | Indicator Removal on Host | Adversaries may attempt to remove indicators of their presence on a system in an effort to cover their tracks. In cases where an adversary may feel detection is imminent, they may try to overwrite, delete, or cover up changes they have made to the device. | https://collaborate.mitre.org/attackics/index.php/Technique/T0872 | 21 May 2020 | 08 October 2021 |  | Evasion Ics | Human-Machine Interface, Safety Instrumented System/Protection Relay | Command: Command Execution, File: File Deletion, File: File Metadata, File: File Modification, Network Traffic: Network Traffic Content, Process: OS API Execution, Process: Process Creation, User Account: User Account Authentication, Windows Registry: Windows Registry Key Deletion, Windows Registry: Windows Registry Key Modification
T0883 | Internet Accessible Device | Adversaries may gain access into industrial environments through systems exposed directly to the internet for remote access rather than through External Remote Services. Internet Accessible Devices are exposed to the internet unintentionally or intentionally without adequate protections. This may allow for adversaries to move directly into the control system network. Access onto these devices is accomplished without the use of exploits, these would be represented within the Exploit Public-Facing Application technique. Adversaries may leverage built in functions for remote access which may not be protected or utilize minimal legacy protections that may be targeted.(Citation: Bowman Dam - ICS-CERT) In the case of the Bowman dam incident, adversaries leveraged access to the dam control network through a cellular modem. Access to the device was protected by password authentication, although the application was vulnerable to brute forcing.(Citation: Bowman Dam - ICS-CERT)(Citation: Bowman Dam - wall street journal)(Citation: owman Dam - Times) In Trend Micro’s manufacturing deception operations adversaries were detected leveraging direct internet access to an ICS environment through the exposure of operational protocols such as Siemens S7, Omron FINS, and EtherNet/IP, in addition to misconfigured VNC access.(Citation: Trend Micro Honeypot) | https://collaborate.mitre.org/attackics/index.php/Technique/T0883 | 21 May 2020 | 08 October 2021 |  | Initial Access Ics | Control Server, Data Historian, Field Controller/RTU/PLC/IED, Human-Machine Interface, Input/Output Server, Safety Instrumented System/Protection Relay | Logon Session: Logon Session Metadata, Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow
T0867 | Lateral Tool Transfer | Adversaries may transfer tools or other files from one system to another to stage adversary tools or other files over the course of an operation. (Citation: EAttack Lateral Tool Transfer) Copying of files may also be performed laterally between internal victim systems to support Lateral Movement with remote Execution using inherent file sharing protocols such as file sharing over SMB to connected network shares. (Citation: EAttack Remote File Copy) In control systems environments, malware may use SMB and other file sharing protocols to move laterally through industrial networks. | https://collaborate.mitre.org/attackics/index.php/Technique/T0867 | 21 May 2020 | 08 October 2021 |  | Lateral Movement Ics | Control Server, Data Historian, Human-Machine Interface | Command: Command Execution, File: File Creation, File: File Metadata, Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow, Process: Process Creation
T0826 | Loss of Availability | Adversaries may attempt to disrupt essential components or systems to prevent owner and operator from delivering products or services. (Citation: Reference - Corero) (Citation: Reference - SANS - 201510) (Citation: Reference - RIoT) Adversaries may leverage malware to delete or encrypt critical data on HMIs, workstations, or databases. In the 2021 Colonial Pipeline ransomware incident, pipeline operations were temporally halted on May 7th and were not fully restarted until May 12th. | https://collaborate.mitre.org/attackics/index.php/Technique/T0826 | 21 May 2020 | 08 October 2021 |  | Impact Ics | Windows
T0827 | Loss of Control | Adversaries may seek to achieve a sustained loss of control or a runaway condition in which operators cannot issue any commands even if the malicious interference has subsided.(Citation: Reference - Corero)(Citation: Reference - SANS - 201510)(Citation: Reference - RIoT) The German Federal Office for Information Security (BSI) reported a targeted attack on a steel mill in its 2014 IT Security Report.(Citation: BSI IT Security Situation 2014) These targeted attacks affected industrial operations and resulted in breakdowns of control system components and even entire installations. As a result of these breakdowns, massive impact resulted in damage and unsafe conditions from the uncontrolled shutdown of a blast furnace. | https://collaborate.mitre.org/attackics/index.php/Technique/T0827 | 21 May 2020 | 21 May 2020 | Dragos Threat Intelligence | Impact Ics | None
T0828 | Loss of Productivity and Revenue | Adversaries may cause loss of productivity and revenue through disruption and even damage to the availability and integrity of control system operations, devices, and related processes. This technique may manifest as a direct effect of an ICS-targeting attack or tangentially, due to an IT-targeting attack against non-segregated environments. In cases where these operations or services are brought to a halt, the loss of productivity may eventually present an impact for the end-users or consumers of products and services. The disrupted supply-chain may result in supply shortages and increased prices, among other consequences. A ransomware attack on an Australian beverage company resulted in the shutdown of some manufacturing sites, including precautionary halts to protect key systems. (Citation: Distrupted Operations at Lion Company June 2020) The company announced the potential for temporary shortages of their products following the attack. (Citation: Distrupted Operations at Lion Company June 2020) (Citation: Lion Cyber Incident June 2020) In the 2021 Colonial Pipeline ransomware incident, the pipeline was unable to transport approximately 2.5 million barrels of fuel per day to the East Coast. (Citation: Colonial Pipeline System Distruption May 2021) | https://collaborate.mitre.org/attackics/index.php/Technique/T0828 | 21 May 2020 | 14 October 2021 |  | Impact Ics | None
T0837 | Loss of Protection | Adversaries may compromise protective system functions designed to prevent the effects of faults and abnormal conditions. This can result in equipment damage, prolonged process disruptions and hazards to personnel. Many faults and abnormal conditions in process control happen too quickly for a human operator to react to. Speed is critical in correcting these conditions to limit serious impacts such as Loss of Control and Property Damage. Adversaries may target and disable protective system functions as a prerequisite to subsequent attack execution or to allow for future faults and abnormal conditions to go unchecked. Detection of a Loss of Protection by operators can result in the shutdown of a process due to strict policies regarding protection systems. This can cause a Loss of Productivity and Revenue and may meet the technical goals of adversaries seeking to cause process disruptions. | https://collaborate.mitre.org/attackics/index.php/Technique/T0837 | 12 April 2021 | 12 April 2021 |  | Impact Ics | None
T0880 | Loss of Safety | Adversaries may compromise safety system functions designed to maintain safe operation of a process when unacceptable or dangerous conditions occur. Safety systems are often composed of the same elements as control systems but have the sole purpose of ensuring the process fails in a predetermined safe manner. Many unsafe conditions in process control happen too quickly for a human operator to react to. Speed is critical in correcting these conditions to limit serious impacts such as Loss of Control and Property Damage. Adversaries may target and disable safety system functions as a prerequisite to subsequent attack execution or to allow for future unsafe conditionals to go unchecked. Detection of a Loss of Safety by operators can result in the shutdown of a process due to strict policies regarding safety systems. This can cause a Loss of Productivity and Revenue and may meet the technical goals of adversaries seeking to cause process disruptions. | https://collaborate.mitre.org/attackics/index.php/Technique/T0880 | 21 May 2020 | 12 April 2021 |  | Impact Ics | None
T0829 | Loss of View | Adversaries may cause a sustained or permanent loss of view where the ICS equipment will require local, hands-on operator intervention; for instance, a restart or manual operation. By causing a sustained reporting or visibility loss, the adversary can effectively hide the present state of operations. This loss of view can occur without affecting the physical processes themselves. (Citation: Reference - Corero) (Citation: Reference - SANS - 201510) (Citation: Reference - RIoT) | https://collaborate.mitre.org/attackics/index.php/Technique/T0829 | 21 May 2020 | 12 April 2021 |  | Impact Ics | Engineering Workstation, Human-Machine Interface
T0830 | Man in the Middle | Adversaries with privileged network access may seek to modify network traffic in real time using man-in-the-middle (MITM) attacks. (Citation: Reference - SANS - 201710) This type of attack allows the adversary to intercept traffic to and/or from a particular device on the network. If a MITM attack is established, then the adversary has the ability to block, log, modify, or inject traffic into the communication stream. There are several ways to accomplish this attack, but some of the most-common are Address Resolution Protocol (ARP) poisoning and the use of a proxy. (Citation: Research - Research - Taxonomy Cyber Attacks on SCADA) A MITM attack may allow an adversary to perform the following attacks: Block Reporting Message, Spoof Reporting Message, Modify Parameter, Unauthorized Command Message | https://collaborate.mitre.org/attackics/index.php/Technique/T0830 | 21 May 2020 | 08 October 2021 | Conrad Layne - GE Digital | Collection Ics | Control Server, Field Controller/RTU/PLC/IED, Human-Machine Interface | Command: Command Execution, Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow, Process: OS API Execution, Process: Process Creation
T0835 | Manipulate I/O Image | Adversaries may manipulate the I/O image of PLCs through various means to prevent them from functioning as expected. Methods of I/O image manipulation may include overriding the I/O table via direct memory manipulation or using the override function used for testing PLC programs. (Citation: Guidance - ISA PLC) During the scan cycle, a PLC reads the status of all inputs and stores them in an image table.2 The image table is the PLC’s internal storage location where values of inputs/outputs for one scan are stored while it executes the user program. After the PLC has solved the entire logic program, it updates the output image table. The contents of this output image table are written to the corresponding output points in I/O Modules. One of the unique characteristics of PLCs is their ability to override the status of a physical discrete input or to override the logic driving a physical output coil and force the output to a desired status. | https://collaborate.mitre.org/attackics/index.php/Technique/T835 | 21 May 2020 | 14 October 2021 |  | Inhibit Response Function | Field Controller/RTU/PLC/IED | Operational Databases: Device Alarm, Operational Databases: Process History/Live Data
T0831 | Manipulation of Control | Adversaries may manipulate physical process control within the industrial environment. Methods of manipulating control can include changes to set point values, tags, or other parameters. Adversaries may manipulate control systems devices or possibly leverage their own, to communicate with and command physical control processes. The duration of manipulation may be temporary or longer sustained, depending on operator detection. Methods of Manipulation of Control include: Man-in-the-middle, Spoof command message, Changing setpoints. A Polish student used a remote controller device to interface with the Lodz city tram system in Poland.(Citation: LondonReconnections Hacked Cyber Security Railways May 2017)(Citation: InHomelandSecurity Hacker Poland February 2008)(Citation: Schneier Hacking Polish Trams January 2008) Using this remote, the student was able to capture and replay legitimate tram signals. As a consequence, four trams were derailed and twelve people injured due to resulting emergency stops.(Citation: InHomelandSecurity Hacker Poland February 2008)Using this remote, the student was able to capture and replay legitimate tram signals. As a consequence, four trams were derailed and twelve people injured due to resulting emergency stops.(Citation: InHomelandSecurity Hacker Poland February 2008) The track controlling commands issued may have also resulted in tram collisions, a further risk to those on board and nearby the areas of impact.(Citation: Schneier Hacking Polish Trams January 2008) | https://collaborate.mitre.org/attackics/index.php/Technique/T0831 | 21 May 2020 | 12 April 2021 |  | Impact Ics | None
T0832 | Manipulation of View | Adversaries may attempt to manipulate the information reported back to operators or controllers. This manipulation may be short term or sustained. During this time the process itself could be in a much different state than what is reported. (Citation: Reference - Corero) (Citation: Reference - SANS - 201510) (Citation: Reference - RIoT) Operators may be fooled into doing something that is harmful to the system in a loss of view situation. With a manipulated view into the systems, operators may issue inappropriate control sequences that introduce faults or catastrophic failures into the system. Business analysis systems can also be provided with inaccurate data leading to bad management decisions. | https://collaborate.mitre.org/attackics/index.php/Technique/T0832 | 21 May 2020 | 12 April 2021 |  | Impact Ics | Engineering Workstation, Field Controller/RTU/PLC/IED, Human-Machine Interface
T0849 | Masquerading | Adversaries may use masquerading to disguise a malicious application or executable as another file, to avoid operator and engineer suspicion. Possible disguises of these masquerading files can include commonly found programs, expected vendor executables and configuration files, and other commonplace application and naming conventions. By impersonating expected and vendor-relevant files and applications, operators and engineers may not notice the presence of the underlying malicious content and possibly end up running those masquerading as legitimate functions. Applications and other files commonly found on Windows systems or in engineering workstations have been impersonated before. This can be as simple as renaming a file to effectively disguise it in the ICS environment. | https://collaborate.mitre.org/attackics/index.php/Technique/T0849 | 21 May 2020 | 08 October 2021 |  | Evasion Ics | Control Server, Human-Machine Interface | Command: Command Execution, File: File Metadata, File: File Modification, Scheduled Job: Scheduled Job Metadata, Scheduled Job: Scheduled Job Modification, Service: Service Creation, Service: Service Metadata
T0838 | Modify Alarm Settings | Adversaries may modify alarm settings to prevent alerts that may inform operators of their presence or to prevent responses to dangerous and unintended scenarios. Reporting messages are a standard part of data acquisition in control systems. Reporting messages are used as a way to transmit system state information and acknowledgements that specific actions have occurred. These messages provide vital information for the management of a physical process, and keep operators, engineers, and administrators aware of the state of system devices and physical processes. If an adversary is able to change the reporting settings, certain events could be prevented from being reported. This type of modification can also prevent operators or devices from performing actions to keep the system in a safe state. If critical reporting messages cannot trigger these actions then a Impact could occur. In ICS environments, the adversary may have to use <span class="smw-format list-format "><span class="smw-row"><span class="smw-field"><span class="smw-value">Alarm Suppression</span></span></span></span> or contend with multiple alarms and/or alarm propagation to achieve a specific goal to evade detection or prevent intended responses from occurring. (Citation: References - Secura - 2019) Methods of suppression often rely on modification of alarm settings, such as modifying in memory code to fixed values or tampering with assembly level instruction code. In the Maroochy Attack, the adversary disabled alarms at four pumping stations. This caused alarms to not be reported to the central computer. (Citation: Maroochy - MITRE - 200808) | https://collaborate.mitre.org/attackics/index.php/Technique/T0838 | 21 May 2020 | 08 October 2021 |  | Inhibit Response Function | Control Server, Device Configuration/Parameters, Field Controller/RTU/PLC/IED, Human-Machine Interface, Safety Instrumented System/Protection Relay | Application Log: Application Log Content, Network Traffic: Network Traffic Content, Operational Databases: Process History/Live Data
T0821 | Modify Controller Tasking | Adversaries may modify the tasking of a controller to allow for the execution of their own programs. This can allow an adversary to manipulate the execution flow and behavior of a controller. According to 61131-3, the association of a Task with a Program Organization Unit (POU) defines a task association. An adversary may modify these associations or create new ones to manipulate the execution flow of a controller. Modification of controller tasking can be accomplished using a Program Download in addition to other types of program modification such as online edit and program append. Tasks have properties, such as interval, frequency and priority to meet the requirements of program execution. Some controller vendors implement tasks with implicit, pre-defined properties whereas others allow for these properties to be formulated explicitly. An adversary may associate their program with tasks that have a higher priority or execute associated programs more frequently. For instance, to ensure cyclic execution of their program on a Siemens controller, an adversary may add their program to the “task”, Organization Block 1 (OB1). | https://collaborate.mitre.org/attackics/index.php/Technique/T0821 | 13 April 2021 | 08 October 2021 |  | Execution Ics | Field Controller/RTU/PLC/IED | Asset: Software/Firmware, File: File Modification
T0836 | Modify Parameter | Adversaries may modify parameters used to instruct industrial control system devices. These devices operate via programs that dictate how and when to perform actions based on such parameters. Such parameters can determine the extent to which an action is performed and may specify additional options. For example, a program on a control system device dictating motor processes may take a parameter defining the total number of seconds to run that motor. An adversary can potentially modify these parameters to produce an outcome outside of what was intended by the operators. By modifying system and process critical parameters, the adversary may cause Impact to equipment and/or control processes. Modified parameters may be turned into dangerous, out-of-bounds, or unexpected values from typical operations. For example, specifying that a process run for more or less time than it should, or dictating an unusually high, low, or invalid value as a parameter. In the Maroochy Attack, Vitek Boden gained remote computer access to the control system and altered data so that whatever function should have occurred at affected pumping stations did not occur or occurred in a different way. The software program installed in the laptop was one developed by Hunter Watertech for its use in changing configurations in the PDS computers. This ultimately led to 800,000 liters of raw sewage being spilled out into the community. (Citation: Maroochy - MITRE - 200808) In the Oldsmar water treatment attack, adversaries raised the sodium hydroxide setpoint value from 100 part-per-million (ppm) to 11,100 ppm, far beyond normal operating levels. (Citation: Oldsmar Water Treatment Attack Feb 2021) | https://collaborate.mitre.org/attackics/index.php/Technique/T0836 | 21 May 2020 | 14 October 2021 |  | Impair Process Control | Control Server, Field Controller/RTU/PLC/IED, Human-Machine Interface, Safety Instrumented System/Protection Relay | Application Log: Application Log Content, Asset: Device Configuration/Parameters, Network Traffic: Network Traffic Content, Operational Databases: Device Alarm
T0889 | Modify Program | Adversaries may modify or add a program on a controller to affect how it interacts with the physical process, peripheral devices and other hosts on the network. Modification to controller programs can be accomplished using a Program Download in addition to other types of program modification such as online edit and program append. Program modification encompasses the addition and modification of instructions and logic contained in Program Organization Units (POU) and similar programming elements found on controllers. This can include, for example, adding new functions to a controller, modifying the logic in existing functions and making new calls from one function to another. Some programs may allow an adversary to interact directly with the native API of the controller to take advantage of obscure features or vulnerabilities. | https://collaborate.mitre.org/attackics/index.php/Technique/T0889 | 13 April 2021 | 08 October 2021 |  | Persistence Ics | Field Controller/RTU/PLC/IED | Asset: Software/Firmware, File: File Modification
T0839 | Module Firmware | Adversaries may install malicious or vulnerable firmware onto modular hardware devices. Control system devices often contain modular hardware devices. These devices may have their own set of firmware that is separate from the firmware of the main control system equipment. This technique is similar to <span class="smw-format list-format "><span class="smw-row"><span class="smw-field"><span class="smw-value">System Firmware</span></span></span></span>, but is conducted on other system components that may not have the same capabilities or level of integrity checking. Although it results in a device re-image, malicious device firmware may provide persistent access to remaining devices. (Citation: References - Module Firmware) An easy point of access for an adversary is the Ethernet card, which may have its own CPU, RAM, and operating system. The adversary may attack and likely exploit the computer on an Ethernet card. Exploitation of the Ethernet card computer may enable the adversary to accomplish additional attacks, such as the following: (Citation: References - Module Firmware) *Delayed Attack - The adversary may stage an attack in advance and choose when to launch it, such as at a particularly damaging time. *Brick the Ethernet Card - Malicious firmware may be programmed to result in an Ethernet card failure, requiring a factory return. *"Random" Attack or Failure - The adversary may load malicious firmware onto multiple field devices. Execution of an attack and the time it occurs is generated by a pseudo-random number generator. *A Field Device Worm - The adversary may choose to identify all field devices of the same model, with the end goal of performing a device-wide compromise. *Attack Other Cards on the Field Device - Although it is not the most important module in a field device, the Ethernet card is most accessible to the adversary and malware. Compromise of the Ethernet card may provide a more direct route to compromising other modules, such as the CPU module. | https://collaborate.mitre.org/attackics/index.php/Technique/T0839 | 21 May 2020 | 08 October 2021 |  | Impair Process Control, Persistence Ics | Field Controller/RTU/PLC/IED, Safety Instrumented System/Protection Relay | Firmware: Firmware Modification, Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow
T0801 | Monitor Process State | Adversaries may gather information about the physical process state. This information may be used to gain more information about the process itself or used as a trigger for malicious actions. The sources of process state information may vary such as, OPC tags, historian data, specific PLC block information, or network traffic. | https://collaborate.mitre.org/attackics/index.php/Technique/T0801 | 21 May 2020 | 08 October 2021 |  | Collection Ics | Control Server, Data Historian, Field Controller/RTU/PLC/IED, Human-Machine Interface, Safety Instrumented System/Protection Relay | Network Traffic: Network Traffic Content
T0834 | Native API | Adversaries may directly interact with the native OS application programming interface (API) to access system functions. Native APIs provide a controlled means of calling low-level OS services within the kernel, such as those involving hardware/devices, memory, and processes.(Citation: EAttack Native API) These native APIs are leveraged by the OS during system boot (when other system components are not yet initialized) as well as carrying out tasks and requests during routine operations. Functionality provided by native APIs are often also exposed to user-mode applications via interfaces and libraries. For example, functions such as memcpy and direct operations on memory registers can be used to modify user and system memory space. | https://collaborate.mitre.org/attackics/index.php/Technique/T0834 | 13 April 2021 | 08 October 2021 |  | Execution Ics | Control Server, Data Historian, Field Controller/RTU/PLC/IED, Human-Machine Interface, Input/Output Server, Safety Instrumented System/Protection Relay | Process: OS API Execution
T0840 | Network Connection Enumeration | Adversaries may perform network connection enumeration to discover information about device communication patterns. If an adversary can inspect the state of a network connection with tools, such as [https://en.wikipedia.org/wiki/Netstat netstat], in conjunction with <span class="smw-format list-format "><span class="smw-row"><span class="smw-field"><span class="smw-value">System Firmware</span></span></span></span>, then they can determine the role of certain devices on the network (Citation: EAttack System Network Connections Discovery). The adversary can also use Network Sniffing to watch network traffic for details about the source, destination, protocol, and content. | https://collaborate.mitre.org/attackics/index.php/Technique/T0840 | 21 May 2020 | 08 October 2021 |  | Discovery Ics | Human-Machine Interface | Command: Command Execution, Process: OS API Execution, Process: Process Creation
T0842 | Network Sniffing | Network sniffing is the practice of using a network interface on a computer system to monitor or capture information (Citation: EAttack Network Sniffing) regardless of whether it is the specified destination for the information. An adversary may attempt to sniff the traffic to gain information about the target. This information can vary in the level of importance. Relatively unimportant information is general communications to and from machines. Relatively important information would be login information. User credentials may be sent over an unencrypted protocol, such as [https://tools.ietf.org/html/rfc854 Telnet], that can be captured and obtained through network packet analysis. Network sniffing can be a way to discover information for <span class="smw-format list-format "><span class="smw-row"><span class="smw-field"><span class="smw-value">Control Device Identification</span></span></span></span>. In addition, ARP and Domain Name Service (DNS) poisoning can be used to capture credentials to websites, proxies, and internal systems by redirecting traffic to an adversary. Detection: Detecting the events leading up to sniffing network traffic may be the best method of detection. From the host level, an adversary would likely need to perform a man-in-the-middle attack against other devices on a wired network in order to capture traffic that was not to or from the current compromised system. This change in the flow of information is detectable at the enclave network level. Monitor for ARP spoofing and gratuitous ARP broadcasts. Detecting compromised network devices is a bit more challenging. Auditing administrator logins, configuration changes, and device images is required to detect malicious changes. | https://collaborate.mitre.org/attackics/index.php/Technique/T0842 | 21 May 2020 | 08 October 2021 |  | Discovery Ics | Field Controller/RTU/PLC/IED | Command: Command Execution, Process: Process Creation
T0861 | Point & Tag Identification | Adversaries may collect point and tag values to gain a more comprehensive understanding of the process environment. Points may be values such as inputs, memory locations, outputs or other process specific variables. (Citation: References - tags process comprehension) Tags are the identifiers given to points for operator convenience. Collecting such tags provides valuable context to environmental points and enables an adversary to map inputs, outputs, and other values to their control processes. Understanding the points being collected may inform an adversary on which processes and values to keep track of over the course of an operation. | https://collaborate.mitre.org/attackics/index.php/Technique/T0861 | 21 May 2020 | 08 October 2021 | Jos Wetzels - Midnight Blue | Collection Ics | Control Server, Data Historian, Human-Machine Interface | Network Traffic: Network Traffic Content
T0843 | Program Download | Adversaries may perform a program download to transfer a user program to a controller. ariations of program download, such as online edit and program append, allow a controller to continue running during the transfer and reconfiguration process without interruption to process control. However, before starting a full program download (i.e., download all) a controller may need to go into a stop state. This can have negative consequences on the physical process, especially if the controller is not able to fulfill a time-sensitive action. Adversaries may choose to avoid a download all in favor of an online edit or program append to avoid disrupting the physical process. An adversary may need to use the technique Detect Operating Mode or Change Operating Mode to make sure the controller is in the proper mode to accept a program download. The granularity of control to transfer a user program in whole or parts is dictated by the management protocol (e.g., S7CommPlus, TriStation) and underlying controller API. Thus, program download is a high-level term for the suite of vendor-specific API calls used to configure a controller’s user program memory space. Modify Controller Tasking and Modify Program represent the configuration changes that are transferred to a controller via a program download. | https://collaborate.mitre.org/attackics/index.php/Technique/T0843 | 21 May 2020 | 08 October 2021 | Joe Slowik - Dragos | Lateral Movement Ics | Field Controller/RTU/PLC/IED, Safety Instrumented System/Protection Relay | Application Log: Application Log Content, Network Traffic: Network Traffic Content, Operational Databases: Device Alarm
T0845 | Program Upload | Adversaries may attempt to upload a program from a PLC to gather information about an industrial process. Uploading a program may allow them to acquire and study the underlying logic. Methods of program upload include vendor software, which enables the user to upload and read a program running on a PLC. This software can be used to upload the target program to a workstation, jump box, or an interfacing device. | https://collaborate.mitre.org/attackics/index.php/Technique/T0845 | 21 May 2020 | 13 October 2021 |  | Collection Ics | Field Controller/RTU/PLC/IED, Safety Instrumented System/Protection Relay | Application Log: Application Log Content, Network Traffic: Network Traffic Content
T0873 | Project File Infection | Adversaries may attempt to infect project files with malicious code. These project files may consist of objects, program organization units, variables such as tags, documentation, and other configurations needed for PLC programs to function. (Citation: References - beckhoff project files) Using built in functions of the engineering software, adversaries may be able to download an infected program to a PLC in the operating environment enabling further execution and persistence techniques. (Citation: References - plcdev siemens) Adversaries may export their own code into project files with conditions to execute at specific intervals. (Citation: Stuxnet - Symantec - 201102) Malicious programs allow adversaries control of all aspects of the process enabled by the PLC. Once the project file is downloaded to a PLC the workstation device may be disconnected with the infected project file still executing. (Citation: References - plcdev siemens) | https://collaborate.mitre.org/attackics/index.php/Technique/T0873 | 21 May 2020 | 08 October 2021 |  | Persistence Ics | Engineering Workstation, Human-Machine Interface | File: File Modification
T0886 | Remote Services | Adversaries may leverage remote services to move between assets and network segments. These services are often used to allow operators to interact with systems remotely within the network, some examples are RDP, SMB, SSH, and other similar mechanisms. Remote services could be used to support remote access, data transmission, authentication, name resolution, and other remote functions. Further, remote services may be necessary to allow operators and administrators to configure systems within the network from their engineering or management workstations. An adversary may use this technique to access devices which may be dual-homed to multiple network segments, and can be used for Program Download or to execute attacks on control devices directly through Valid Accounts. Specific remote services (RDP & VNC) may be a precursor to enable Graphical User Interface execution on devices such as HMIs or engineering workstation software. In the Oldsmar water treatment attack, adversaries gained access to the system through remote access software, allowing for the use of the standard operator HMI interface.(Citation: Oldsmar Water Treatment Attack Feb 2021) Based on incident data, CISA and FBI assessed that Chinese state-sponsored actors also compromised various authorized remote access channels, including systems designed to transfer data and/or allow access between corporate and ICS networks.(Citation: CISA Chinese Gas Pipeline Intrusion 2011 - 2013 July 2021) | https://collaborate.mitre.org/attackics/index.php/Technique/T0886 | 12 April 2021 | 08 October 2021 |  | Initial Access Ics, Lateral Movement Ics | Control Server, Engineering Workstation, Human-Machine Interface | Command: Command Execution, Logon Session: Logon Session Creation, Network Share: Network Share Access, Network Traffic: Network Connection Creation, Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow, Process: Process Creation
T0846 | Remote System Discovery | Adversaries may attempt to get a listing of other systems by IP address, hostname, or other logical identifier on a network that may be used for subsequent Lateral Movement or Discovery techniques. Functionality could exist within adversary tools to enable this, but utilities available on the operating system or vendor software could also be used.(Citation: EAttack Remote System Discovery) | https://collaborate.mitre.org/attackics/index.php/Technique/T0846 | 21 May 2020 | 08 October 2021 |  | Discovery Ics | Control Server, Data Historian, Field Controller/RTU/PLC/IED, Human-Machine Interface, Safety Instrumented System/Protection Relay | Command: Command Execution, File: File Access, Network Traffic: Network Connection Creation, Process: Process Creation
T0888 | Remote System Information Discovery | An adversary may attempt to get detailed information about remote systems and their peripherals, such as make/model, role, and configuration. Adversaries may use information from Remote System Information Discovery to aid in targeting and shaping follow-on behaviors. For example, the system’s operational role and model information can dictate whether it is a relevant target for the adversary’s operational objectives. In addition, the system’s configuration may be used to scope subsequent technique usage. Requests for system information are typically implemented using automation and management protocols and are often automatically requested by vendor software during normal operation. This information may be used to tailor management actions, such as program download and system or module firmware. An adversary may leverage this same information by issuing calls directly to the system’s API. | https://collaborate.mitre.org/attackics/index.php/Technique/T0888 | 13 April 2021 | 08 October 2021 |  | Discovery Ics | Field Controller/RTU/PLC/IED, Safety Instrumented System/Protection Relay | Application Log: Application Log Content, Network Traffic: Network Traffic Content
T0847 | Replication Through Removable Media | Adversaries may move onto systems, such as those separated from the enterprise network, by copying malware to removable media which is inserted into the control systems environment. The adversary may rely on unknowing trusted third parties, such as suppliers or contractors with access privileges, to introduce the removable media. This technique enables initial access to target devices that never connect to untrusted networks, but are physically accessible. Operators of the German nuclear power plant, Gundremmingen, discovered malware on a facility computer not connected to the internet. (Citation: KGG-Company-Site) (Citation: KGG-Trend Micro) The malware included Conficker and W32.Ramnit, which were also found on eighteen removable disk drives in the facility. (Citation: KGG-Reuters) (Citation: KGG-Softpedia) (Citation: KGG-Science-Alert) (Citation: KGG-Geek) (Citation: KGG-Ars) (Citation: KGG-Dark) The plant has since checked for infection and cleaned up more than 1,000 computers. (Citation: KGG-BBC) An ESET researcher commented that internet disconnection does not guarantee system safety from infection or payload execution. (Citation: KGG-ESET) | https://collaborate.mitre.org/attackics/index.php/Technique/T0847 | 21 May 2020 | 08 October 2021 |  | Initial Access Ics | Control Server, Data Historian, Human-Machine Interface | Drive: Drive Creation, File: File Access, File: File Creation, Process: Process Creation
T0848 | Rogue Master | Adversaries may setup a rogue master to leverage control server functions to communicate with outstations. A rogue master can be used to send legitimate control messages to other control system devices, affecting processes in unintended ways. It may also be used to disrupt network communications by capturing and receiving the network traffic meant for the actual master. Impersonating a master may also allow an adversary to avoid detection. In the Maroochy Attack, Vitek Boden falsified network addresses in order to send false data and instructions to pumping stations. In the case of the 2017 Dallas Siren incident, adversaries used a rogue master to send command messages to the 156 distributed sirens across the city, either through a single rogue transmitter with a strong signal, or using many distributed repeaters. | https://collaborate.mitre.org/attackics/index.php/Technique/T0848 | 21 May 2020 | 08 October 2021 |  | Initial Access Ics | Control Server, Engineering Workstation, Human-Machine Interface | Application Log: Application Log Content, Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow, Operational Databases: Process/Event Alarm
T0851 | Rootkit | Adversaries may deploy rootkits to hide the presence of programs, files, network connections, services, drivers, and other system components. Rootkits are programs that hide the existence of malware by intercepting and modifying operating-system API calls that supply system information. Rootkits or rootkit-enabling functionality may reside at the user or kernel level in the operating system, or lower. (Citation: EAttack Rootkit) Firmware rootkits that affect the operating system yield nearly full control of the system. While firmware rootkits are normally developed for the main processing board, they can also be developed for I/O that can be attached to the asset. Compromise of this firmware allows the modification of all of the process variables and functions the module engages in. This may result in commands being disregarded and false information being fed to the main device. By tampering with device processes, an adversary may inhibit its expected response functions and possibly enable Impact. Detection: Some rootkit protections may be built into anti-virus or operating system software. There are dedicated rootkit detection tools that look for specific types of rootkit behavior. Monitor for the existence of unrecognized DLLs, devices, services, and changes to the MBR.Reference - Rootkit | https://collaborate.mitre.org/attackics/index.php/Technique/T0851 | 21 May 2020 | 08 October 2021 |  | Evasion Ics, Inhibit Response Function | Field Controller/RTU/PLC/IED | Drive: Drive Modification, Firmware: Firmware Modification, Module: Module Load
T0852 | Screen Capture | Adversaries may attempt to perform screen capture of devices in the control system environment. Screenshots may be taken of workstations, HMIs, or other devices that display environment-relevant process, device, reporting, alarm, or related data. These device displays may reveal information regarding the ICS process, layout, control, and related schematics. In particular, an HMI can provide a lot of important industrial process information. (Citation: Alert - Russian APT TA18-074A - 201803) Analysis of screen captures may provide the adversary with an understanding of intended operations and interactions between critical devices. | https://collaborate.mitre.org/attackics/index.php/Technique/T0852 | 21 May 2020 | 08 October 2021 |  | Collection Ics | Human-Machine Interface | Command: Command Execution, Process: OS API Execution
T0853 | Scripting | Adversaries may use scripting languages to execute arbitrary code in the form of a pre-written script or in the form of user-supplied code to an interpreter. Scripting languages are programming languages that differ from compiled languages, in that scripting languages use an interpreter, instead of a compiler. These interpreters read and compile part of the source code just before it is executed, as opposed to compilers, which compile each and every line of code to an executable file. Scripting allows software developers to run their code on any system where the interpreter exists. This way, they can distribute one package, instead of precompiling executables for many different systems. Scripting languages, such as Python, have their interpreters shipped as a default with many Linux distributions. In addition to being a useful tool for developers and administrators, scripting language interpreters may be abused by the adversary to execute code in the target environment. Due to the nature of scripting languages, this allows for weaponized code to be deployed to a target easily, and leaves open the possibility of on-the-fly scripting to perform a task. | https://collaborate.mitre.org/attackics/index.php/Technique/T0853 | 21 May 2020 | 08 October 2021 |  | Execution Ics | Engineering Workstation | Command: Command Execution, Module: Module Load, Process: Process Creation, Script: Script Execution
T0881 | Service Stop | Adversaries may stop or disable services on a system to render those services unavailable to legitimate users. Stopping critical services can inhibit or stop response to an incident or aid in the adversary's overall objectives to cause damage to the environment. (Citation: EAttack Service Stop) Services may not allow for modification of their data stores while running. Adversaries may stop services in order to conduct Data Destruction. (Citation: EAttack Service Stop) | https://collaborate.mitre.org/attackics/index.php/Technique/T0881 | 21 May 2020 | 08 October 2021 |  | Inhibit Response Function | Control Server, Data Historian, Engineering Workstation, Human-Machine Interface | Command: Command Execution, File: File Modification, Process: OS API Execution, Process: Process Creation, Process: Process Termination, Service: Service Metadata, Windows Registry: Windows Registry Key Modification
T0865 | Spearphishing Attachment | Adversaries may use a spearphishing attachment, a variant of spearphishing, as a form of a social engineering attack against specific targets. Spearphishing attachments are different from other forms of spearphishing in that they employ malware attached to an email. All forms of spearphishing are electronically delivered and target a specific individual, company, or industry. In this scenario, adversaries attach a file to the spearphishing email and usually rely upon User Execution to gain execution and access. (Citation: EAttack Spearphishing Attachment) A Chinese spearphishing campaign running from December 9, 2011 through February 29, 2012, targeted ONG organizations and their employees. The emails were constructed with a high level of sophistication to convince employees to open the malicious file attachments.(Citation: CISA Chinese Gas Pipeline Intrusion 2011 - 2013 July 2021) | https://collaborate.mitre.org/attackics/index.php/Technique/T0865 | 21 May 2020 | 08 October 2021 |  | Initial Access Ics | Control Server, Data Historian, Engineering Workstation, Human-Machine Interface | Application Log: Application Log Content, Network Traffic: Network Traffic Content
T0856 | Spoof Reporting Message | Adversaries may spoof reporting messages in control systems environments to achieve evasion and assist with impairment of process controls. Reporting messages are used in control systems so that operators and network defenders can understand the status of the network. Reporting messages show the status of devices and any important events that the devices control. If an adversary has the ability to Spoof Reporting Messages, then they can impact the network in many ways. The adversary can Spoof Reporting Messages that state that the device is in normal working condition, as a form of evasion. The adversary could also Spoof Reporting Messages to make the defenders and operators think that other errors were occurring, to distract them from the actual source of the problem. (Citation: Research - Research - Taxonomy Cyber Attacks on SCADA) In the Maroochy Attack, the adversary used a dedicated analog two-way radio system to send false data and instructions to pumping stations and the central computer. (Citation: Maroochy - MITRE - 200808) | https://collaborate.mitre.org/attackics/index.php/Technique/T0856 | 21 May 2020 | 08 October 2021 |  | Evasion Ics, Impair Process Control | Control Server | Application Log: Application Log Content, Network Traffic: Network Traffic Content
T0869 | Standard Application Layer Protocol | Adversaries may establish command and control capabilities over commonly used application layer protocols such as HTTP(S), OPC, RDP, telnet, DNP3, and modbus. These protocols may be used to disguise adversary actions as benign network traffic. Standard protocols may be seen on their associated port or in some cases over a non-standard port. Adversaries may use these protocols to reach out of the network for command and control, or in some cases to other infected devices within the network. | https://collaborate.mitre.org/attackics/index.php/Technique/T0869 | 21 May 2020 | 08 October 2021 |  | Command And Control Ics | Control Server, Data Historian, Engineering Workstation, Human-Machine Interface | Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow
T0862 | Supply Chain Compromise | Adversaries may perform supply chain compromise to gain control systems environment access by means of infected products, software, and workflows. Supply chain compromise is the manipulation of products, such as devices or software, or their delivery mechanisms before receipt by the end consumer. Adversary compromise of these products and mechanisms is done for the goal of data or system compromise, once infected products are introduced to the target environment. Supply chain compromise can occur at all stages of the supply chain, from manipulation of development tools and environments to manipulation of developed products and tools distribution mechanisms. This may involve the compromise and replacement of legitimate software and patches, such as on third party or vendor websites. Targeting of supply chain compromise can be done in attempts to infiltrate the environments of a specific audience. In control systems environments with assets in both the IT and OT networks, it is possible a supply chain compromise affecting the IT environment could enable further access to the OT environment. Counterfeit devices may be introduced to the global supply chain posing safety and cyber risks to asset owners and operators. These devices may not meet the safety, engineering and manufacturing requirements of regulatory bodies but may feature tagging indicating conformance with industry standards. Due to the lack of adherence to standards and overall lesser quality, the counterfeit products may pose a serious safety and operational risk. Yokogawa identified instances in which their customers received counterfeit differential pressure transmitters using the Yokogawa logo. The counterfeit transmitters were nearly indistinguishable with a semblance of functionality and interface that mimics the genuine product. F-Secure Labs analyzed the approach the adversary used to compromise victim systems with Havex. (Citation: (Citation: Havex - F-Secure) - 201406) The adversary planted trojanized software installers available on legitimate ICS/SCADA vendor websites. After being downloaded, this software infected the host computer with a Remote Access Trojan (RAT). | https://collaborate.mitre.org/attackics/index.php/Technique/T0862 | 21 May 2020 | 11 October 2021 |  | Initial Access Ics | Control Server, Data Historian, Field Controller/RTU/PLC/IED, Human-Machine Interface, Input/Output Server, Safety Instrumented System/Protection Relay
T0857 | System Firmware | System firmware on modern assets is often designed with an update feature. Older device firmware may be factory installed and require special reprograming equipment. When available, the firmware update feature enables vendors to remotely patch bugs and perform upgrades. Device firmware updates are often delegated to the user and may be done using a software update package. It may also be possible to perform this task over the network. An adversary may exploit the firmware update feature on accessible devices to upload malicious or out-of-date firmware. Malicious modification of device firmware may provide an adversary with root access to a device, given firmware is one of the lowest programming abstraction layers.(Citation: Research - Firmware Modification) | https://collaborate.mitre.org/attackics/index.php/Technique/T0857 | 21 May 2020 | 08 October 2021 |  | Inhibit Response Function, Persistence Ics | Field Controller/RTU/PLC/IED, Input/Output Server, Safety Instrumented System/Protection Relay | Firmware: Firmware Modification, Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow
T0882 | Theft of Operational Information | Adversaries may steal operational information on a production environment as a direct mission outcome for personal gain or to inform future operations. This information may include design documents, schedules, rotational data, or similar artifacts that provide insight on operations. In the Bowman Dam incident, adversaries probed systems for operational data. (Citation: Bowman Dam - Times) (Citation: Bowman Dam - wall street journal) | https://collaborate.mitre.org/attackics/index.php/Technique/T0882 | 21 May 2020 | 11 October 2021 |  | Impact Ics | None
T0864 | Transient Cyber Asset | Adversaries may target devices that are transient across ICS networks and external networks. Normally, transient assets are brought into an environment by authorized personnel and do not remain in that environment on a permanent basis. (Citation: NERC June 2021) Transient assets are commonly needed to support management functions and may be more common in systems where a remotely managed asset is not feasible, external connections for remote access do not exist, or 3rd party contractor/vendor access is required. Adversaries may take advantage of transient assets in different ways. For instance, adversaries may target a transient asset when it is connected to an external network and then leverage its trusted access in another environment to launch an attack. They may also take advantage of installed applications and libraries that are used by legitimate end-users to interact with control system devices. Transient assets, in some cases, may not be deployed with a secure configuration leading to weaknesses that could allow an adversary to propagate malicious executable code, e.g., the transient asset may be infected by malware and when connected to an ICS environment the malware propagates onto other systems. In the Maroochy attack, the adversary utilized a computer, possibly stolen, with proprietary engineering software to communicate with a wastewater system. (Citation: Maroochy - MITRE - 200808) | https://collaborate.mitre.org/attackics/index.php/Technique/T0864 | 14 October 2021 | 14 October 2021 |  | Initial Access Ics | Engineering Workstation | Assets: Asset Inventory, Network Traffic: Network Connections, Network Traffic: Network Flows
T0855 | Unauthorized Command Message | Adversaries may send unauthorized command messages to instruct control system assets to perform actions outside of their intended functionality, or without the logical preconditions to trigger their expected function. Command messages are used in ICS networks to give direct instructions to control systems devices. If an adversary can send an unauthorized command message to a control system, then it can instruct the control systems device to perform an action outside the normal bounds of the device's actions. An adversary could potentially instruct a control systems device to perform an action that will cause an Impact. (Citation: Research - Research - Taxonomy Cyber Attacks on SCADA) In the Maroochy Attack, the adversary used a dedicated analog two-way radio system to send false data and instructions to pumping stations and the central computer. (Citation: Maroochy - MITRE - 200808) In the Dallas Siren incident, adversaries were able to send command messages to activate tornado alarm systems across the city without an impending tornado or other disaster. (Citation:ZDNet Dallas April 2017) (Citation:StateScoop Dallas March 2019) | https://collaborate.mitre.org/attackics/index.php/Technique/T0855 | 21 May 2020 | 08 October 2021 |  | Impair Process Control | Field Controller/RTU/PLC/IED | Application Log: Application Log Content, Network Traffic: Network Traffic Content, Operational Databases: Process History/Live Data, Operational Databases: Process/Event Alarm
T0863 | User Execution | Adversaries may rely on a targeted organizations' user interaction for the execution of malicious code. User interaction may consist of installing applications, opening email attachments, or granting higher permissions to documents. Adversaries may embed malicious code or visual basic code into files such as Microsoft Word and Excel documents or software installers. (Citation: BlackEnergy - Booz Allen Hamilton) Execution of this code requires that the user enable scripting or write access within the document. Embedded code may not always be noticeable to the user especially in cases of trojanized software. (Citation: Havex - F-Secure) A Chinese spearphishing campaign running from December 9, 2011 through February 29, 2012 delivered malware through spearphishing attachments which required user action to achieve execution.(Citation: CISA Chinese Gas Pipeline Intrusion 2011 - 2013 July 2021) | https://collaborate.mitre.org/attackics/index.php/Technique/T0863 | 21 May 2020 | 08 October 2021 |  | Execution Ics | Engineering Workstation, Human-Machine Interface | Application Log: Application Log Content, Command: Command Execution, File: File Creation, Network Traffic: Network Connection Creation, Network Traffic: Network Traffic Content, Process: Process Creation
T0859 | Valid Accounts | Adversaries may steal the credentials of a specific user or service account using credential access techniques. In some cases, default credentials for control system devices may be publicly available. Compromised credentials may be used to bypass access controls placed on various resources on hosts and within the network, and may even be used for persistent access to remote systems. Compromised and default credentials may also grant an adversary increased privilege to specific systems and devices or access to restricted areas of the network. Adversaries may choose not to use malware or tools, in conjunction with the legitimate access those credentials provide, to make it harder to detect their presence or to control devices and send legitimate commands in an unintended way. Adversaries may also create accounts, sometimes using predefined account names and passwords, to provide a means of backup access for persistence.(Citation: BlackEnergy - Booz Allen Hamilton) The overlap of credentials and permissions across a network of systems is of concern because the adversary may be able to pivot across accounts and systems to reach a high level of access (i.e., domain or enterprise administrator) and possibly between the enterprise and operational technology environments. Adversaries may be able to leverage valid credentials from one system to gain access to another system. | https://collaborate.mitre.org/attackics/index.php/Technique/T0859 | 21 May 2020 | 08 October 2021 |  | Lateral Movement Ics, Persistence Ics | Control Server, Data Historian, Engineering Workstation, Field Controller/RTU/PLC/IED, Human-Machine Interface, Input/Output Server, Safety Instrumented System/Protection Relay | Logon Session: Logon Session Creation, User Account: User Account Authentication
T0860 | Wireless Compromise | Adversaries may perform wireless compromise as a method of gaining communications and unauthorized access to a wireless network. Access to a wireless network may be gained through the compromise of a wireless device. (Citation: ICSCorsair - Bolshev) (Citation: Hart - Bolshev) Adversaries may also utilize radios and other wireless communication devices on the same frequency as the wireless network. Wireless compromise can be done as an initial access vector from a remote distance. A joint case study on the Maroochy Shire Water Services event examined the attack from a cyber security perspective. (Citation: Maroochy - MITRE - 200808) The adversary disrupted Maroochy Shire's radio-controlled sewage system by driving around with stolen radio equipment and issuing commands with them. Boden used a two-way radio to communicate with and set the frequencies of Maroochy Shire's repeater stations. A Polish student used a modified TV remote controller to gain access to and control over the Lodz city tram system in Poland. (Citation: LodzTram-LondonReconnections-2017-12) (Citation: LodzTram-InHomelandSecurity-2008-02) The remote controller device allowed the student to interface with the tram’s network to modify track settings and override operator control. The adversary may have accomplished this by aligning the controller to the frequency and amplitude of IR control protocol signals. (Citation: LodzTram-Schneier-2008-01) The controller then enabled initial access to the network, allowing the capture and replay of tram signals. (Citation: LodzTram-LondonReconnections-2017-12) | https://collaborate.mitre.org/attackics/index.php/Technique/T0860 | 21 May 2020 | 08 October 2021 | Scott Dougherty | Initial Access Ics | Control Server, Field Controller/RTU/PLC/IED, Input/Output Server | Application Log: Application Log Content, Logon Session: Logon Session Creation, Network Traffic: Network Traffic Flow
T0887 | Wireless Sniffing | Adversaries may seek to capture radio frequency (RF) communication used for remote control and reporting in distributed environments. RF communication frequencies vary between 3 kHz to 300 GHz, although are commonly between 300 MHz to 6 GHz. The wavelength and frequency of the signal affect how the signal propagates through open air, obstacles (e.g. walls and trees) and the type of radio required to capture them. These characteristics are often standardized in the protocol and hardware and may have an effect on how the signal is captured. Some examples of wireless protocols that may be found in cyber-physical environments are: WirelessHART, Zigbee, WIA-FA, and 700 MHz Public Safety Spectrum. Adversaries may capture RF communications by using specialized hardware, such as software defined radio (SDR), handheld radio, or a computer with radio demodulator tuned to the communication frequency. Information transmitted over a wireless medium may be captured in-transit whether the sniffing device is the intended destination or not. This technique may be particularly useful to an adversary when the communications are not encrypted. In the 2017 Dallas Siren incident, it is suspected that adversaries likely captured wireless command message broadcasts on a 700 MHz frequency during a regular test of the system. These messages were later replayed to trigger the alarm systems. | https://collaborate.mitre.org/attackics/index.php/Technique/T0887 | 21 May 2020 | 12 April 2021 | ICSCoE Japan | Collection Ics, Discovery Ics | None

## procedure examples
source ID | source name | source type | mapping type | target name | target type | mapping description
| ALLANITE | group | uses | Drive-by Compromise | technique | [ALLANITE](https://collaborate.mitre.org/attackics/index.php/Group/G0009) leverages watering hole attacks to gain access into electric utilities.(Citation: SecurityWeek Allanite May 2018)
| ALLANITE | group | uses | Screen Capture | technique | [ALLANITE](https://collaborate.mitre.org/attackics/index.php/Group/G0009) has been identified to collect and distribute screenshots of ICS systems such as HMIs.(Citation: Dragos Allanite)(Citation: CISA Alert (TA17-293A))
| ALLANITE | group | uses | Spearphishing Attachment | technique | [ALLANITE](https://collaborate.mitre.org/attackics/index.php/Group/G0009) utilized spear phishing to gain access into energy sector environments.(Citation: E-ISAC Allanite May 2018)
| ALLANITE | group | uses | Valid Accounts | technique | [ALLANITE](https://collaborate.mitre.org/attackics/index.php/Group/G0009) utilized credentials collected through phishing and watering hole attacks.(Citation: Dragos Allanite)
G0064 | APT33 | group | uses | Screen Capture | technique | [APT33](https://collaborate.mitre.org/attackics/index.php/Group/G0003) utilize backdoors capable of capturing screenshots once installed on a system.(Citation: FireEye APT33 Sept 2017)(Citation: Symantec Trojan.Stonedrill Mar 2017)
G0064 | APT33 | group | uses | Scripting | technique | [APT33](https://collaborate.mitre.org/attackics/index.php/Group/G0003) utilized PowerShell scripts to establish command and control and install files for execution.(Citation: Symantec Elfin Mar 2019)(Citation: Dragos Magnallium)
G0064 | APT33 | group | uses | Spearphishing Attachment | technique | [APT33](https://collaborate.mitre.org/attackics/index.php/Group/G0003) sent spear phishing emails containing links to HTML application files, which were embedded with malicious code.(Citation: FireEye APT33 Sept 2017) APT33 has conducted targeted spear phishing campaigns against U.S. government agencies and private sector companies.(Citation: Wired Jun 2019)
G0035 | Dragonfly | group | uses | Commonly Used Port | technique | [Dragonfly](https://collaborate.mitre.org/attackics/index.php/Group/G0002) communicated with command and control over TCP ports 445 and 139 or UDP 137 or 138.(Citation: CISA Alert (TA17-293A)
G0035 | Dragonfly | group | uses | Drive-by Compromise | technique | [Dragonfly](https://collaborate.mitre.org/attackics/index.php/Group/G0002) used intermediate targets for watering hole attacks on an intended target. A line of code is injected into the header.php file, this is used to redirect the visitors to an adversary controlled IP.(Citation: CISA Alert (TA17-293A)
G0035 | Dragonfly | group | uses | Screen Capture | technique | [Dragonfly](https://collaborate.mitre.org/attackics/index.php/Group/G0002) has been reported to take screenshots of the GUI for ICS equipment, such as HMIs.(Citation: CISA Alert (TA17-293A)
G0035 | Dragonfly | group | uses | Spearphishing Attachment | technique | [Dragonfly](https://collaborate.mitre.org/attackics/index.php/Group/G0002) sent pdf documents over email which contained links to malicious sites and downloads.(Citation: CISA Alert (TA17-293A)
G0035 | Dragonfly | group | uses | Valid Accounts | technique | [Dragonfly](https://collaborate.mitre.org/attackics/index.php/Group/G0002) leveraged compromised user credentials to access the targets networks and download tools from a remote server.(Citation: CISA Alert (TA17-293A)
G0074 | Dragonfly 2.0 | group | uses | Commonly Used Port | technique | [Dragonfly 2.0](https://collaborate.mitre.org/attackics/index.php/Group/G0006) communicated with command and control over TCP ports 445 and 139 or UDP 137 or 138.(Citation: CISA TA18-074A March 2018)
G0074 | Dragonfly 2.0 | group | uses | Data from Information Repositories | technique | [Dragonfly 2.0](https://collaborate.mitre.org/attackics/index.php/Group/G0006) accessed workstations and servers within the corporate network that contained data from power generation control system environments. The files were related to the ICS and SCADA systems including vendor names and ICS reference documents such as wiring diagrams and panel layouts.(Citation: CISA TA18-074A March 2018)
G0074 | Dragonfly 2.0 | group | uses | Drive-by Compromise | technique | [Dragonfly 2.0](https://collaborate.mitre.org/attackics/index.php/Group/G0006) utilized watering hole attacks to gather credentials, by compromising websites that energy sector organizations might access.(Citation: Symantec Dragonfly Sept 2017)
G0074 | Dragonfly 2.0 | group | uses | Indicator Removal on Host | technique | [Dragonfly 2.0](https://collaborate.mitre.org/attackics/index.php/Group/G0006) deleted indicators on staging and target devices by uninstalling software, removing event logs, batch scripts, screenshots, registry keys, documents, and tools they brought into the target networks.(Citation: CISA TA18-074A March 2018)
G0074 | Dragonfly 2.0 | group | uses | Screen Capture | technique | [Dragonfly 2.0](https://collaborate.mitre.org/attackics/index.php/Group/G0006) has been reported to take screenshots of the GUI for ICS equipment, such as HMIs.(Citation: CISA TA18-074A March 2018)
G0074 | Dragonfly 2.0 | group | uses | Scripting | technique | [Dragonfly 2.0](https://collaborate.mitre.org/attackics/index.php/Group/G0006) deleted indicators on staging and target devices by uninstalling software, removing event logs, batch scripts, screenshots, registry keys, documents, and tools they brought into the target networks.(Citation: CISA TA18-074A March 2018)
G0074 | Dragonfly 2.0 | group | uses | Spearphishing Attachment | technique | [Dragonfly 2.0](https://collaborate.mitre.org/attackics/index.php/Group/G0006) used the Phishery tool kit to conduct spear phishing attacks and gather credentials.(Citation: Symantec Dragonfly Sept 2017)(Citation: Talos Jul 2017) Dragonfly 2.0 conducted a targeted spear phishing campaign against multiple electric utilities in the North America.(Citation: Dragos Sept 2018)(Citation: Dragos 2018)
G0074 | Dragonfly 2.0 | group | uses | Supply Chain Compromise | technique | [Dragonfly 2.0](https://collaborate.mitre.org/attackics/index.php/Group/G0006) trojanized legitimate software to deliver malware disguised as standard windows applications.(Citation: Symantec Dragonfly Sept 2017)
G0074 | Dragonfly 2.0 | group | uses | Theft of Operational Information | technique | [Dragonfly 2.0](https://collaborate.mitre.org/attackics/index.php/Group/G0006) captured ICS vendor names, reference documents, wiring diagrams, and panel layouts about the process environment.(Citation: CISA TA18-074A March 2018)
G0074 | Dragonfly 2.0 | group | uses | Valid Accounts | technique | [Dragonfly 2.0](https://collaborate.mitre.org/attackics/index.php/Group/G0006) Dragonfly 2.0 used credentials collected through spear phishing and watering hole attacks.(Citation: Symantec Dragonfly Sept 2017)
| HEXANE | group | uses | Scripting | technique | [HEXANE](https://collaborate.mitre.org/attackics/index.php/Group/G0005) utilizes VBA macros and Powershell scripts such as DanDrop and kl.ps1 tools.(Citation: SecurityWeek Hexane Aug 2019)(Citation: BankInfoSecurity Lyceum Aug 2019)
| HEXANE | group | uses | Spearphishing Attachment | technique | [HEXANE](https://collaborate.mitre.org/attackics/index.php/Group/G0005) has used malicious documents to drop malware and gain access into an environment.(Citation: Dragos Hexane)
| HEXANE | group | uses | Standard Application Layer Protocol | technique | [HEXANE](https://collaborate.mitre.org/attackics/index.php/Group/G0005) communicated with command and control over HTTP and DNS.(Citation: Dragos Hexane)
| HEXANE | group | uses | Valid Accounts | technique | [HEXANE](https://collaborate.mitre.org/attackics/index.php/Group/G0005) has used valid IT accounts to extend their spearphishing campaign within an organization.(Citation: SecureWorks LYCEUM Aug 2019)
G0032 | Lazarus Group | group | uses | Spearphishing Attachment | technique | [Lazarus Group](https://collaborate.mitre.org/attackics/index.php/Group/G0008) has been observed targeting organizations using spearphishing documents with embedded malicious payloads.(Citation: Novetta Blockbuster) Highly targeted spear phishing campaigns have been conducted against a U.S. electric grid company.(Citation: Dragos Mar 2018)
G0049 | OilRig | group | uses | Drive-by Compromise | technique | [OilRig](https://collaborate.mitre.org/attackics/index.php/Group/G0010) has been seen utilizing watering hole attacks to collect credentials which could be used to gain access into ICS networks.(Citation: CyberViser May 21)
G0049 | OilRig | group | uses | Scripting | technique | [OilRig](https://collaborate.mitre.org/attackics/index.php/Group/G0010) has embedded a macro within spearphishing attachments that has been made up of both a VBScript and a PowerShell script.(Citation: PaloAlto OilRig May 2016)
G0049 | OilRig | group | uses | Spearphishing Attachment | technique | [OilRig](https://collaborate.mitre.org/attackics/index.php/Group/G0010) used spearphishing emails with malicious Microsoft Excel spreadsheet attachments.(Citation: PaloAlto OilRig May 2016)
G0049 | OilRig | group | uses | Standard Application Layer Protocol | technique | [OilRig](https://collaborate.mitre.org/attackics/index.php/Group/G0010) communicated with its command and control using HTTP requests.(Citation: PaloAlto OilRig May 2016)
G0049 | OilRig | group | uses | Valid Accounts | technique | [OilRig](https://collaborate.mitre.org/attackics/index.php/Group/G0010) utilized stolen credentials to gain access to victim machines.
G0034 | Sandworm Team | group | uses | Block Command Message | technique | In the Ukraine 2015 Incident, [Sandworm Team](https://collaborate.mitre.org/attackics/index.php/Group/G0007) blocked command messages by using malicious firmware to render communication devices inoperable.(Citation: ICS SANS Ukraine March 2018)
G0034 | Sandworm Team | group | uses | Block Reporting Message | technique | In the Ukraine 2015 Incident, [Sandworm Team](https://collaborate.mitre.org/attackics/index.php/Group/G0007) blocked reporting messages by using malicious firmware to render communication devices inoperable.(Citation: ICS SANS Ukraine March 2018)
G0034 | Sandworm Team | group | uses | Command-Line Interface | technique | [Sandworm Team](https://collaborate.mitre.org/attackics/index.php/Group/G0007) uses the MS-SQL server xp_cmdshell command, and PowerShell to execute commands. (Citation: Dragos CRASHOVERRIDE Oct 2018)
G0034 | Sandworm Team | group | uses | Connection Proxy | technique | [Sandworm Team](https://collaborate.mitre.org/attackics/index.php/Group/G0007) Sandworm Team establishes an internal proxy prior to the installation of backdoors within the network.
G0034 | Sandworm Team | group | uses | Device Restart/Shutdown | technique | In the 2015 attack on the Uktranian power grid, the [Sandworm Team](https://collaborate.mitre.org/attackics/index.php/Group/G0007) scheduled disconnects of uninterruptable power supply (UPS) systems so that when power was disconnected from the substations, the devices would shut down and service could not be recovered.(Citation: ICS SANS Ukraine March 2018)
G0034 | Sandworm Team | group | uses | Exploit Public-Facing Application | technique | [Sandworm Team](https://collaborate.mitre.org/attackics/index.php/Group/G0007) actors exploited vulnerabilities in GE's Cimplicity HMI and Advantech/Broadwin WebAccess HMI software which had been directly exposed to the internet.(Citation: ICS-CERT ICS-Alert-14-281-01E December 2014)(Citation: ICS-CERT Advantech/Broadwin WebAccess RPC Vulnerability September 2018)
G0034 | Sandworm Team | group | uses | External Remote Services | technique | In the Ukraine 2015 Incident, [Sandworm Team](https://collaborate.mitre.org/attackics/index.php/Group/G0007) harvested VPN worker credentials and used them to remotely log into control system networks.(Citation: ICS SANS Ukraine March 2018)
G0034 | Sandworm Team | group | uses | Graphical User Interface | technique | In the Ukraine 2015 Incident, [Sandworm Team](https://collaborate.mitre.org/attackics/index.php/Group/G0007) utilized HMI GUIs in the SCADA environment to open breakers.(Citation: ICS SANS Ukraine March 2018)
G0034 | Sandworm Team | group | uses | Lateral Tool Transfer | technique | [Sandworm Team] (https://collaborate.mitre.org/attackics/index.php/Group/G0007) used a VBS script to facilitate lateral tool transfer. The VBS script was used to copy ICS-specific payloads with the following command: cscript C:/Backinfo/ufn.vbs <TargetIP> “C://Backinfo//101.dll” “C:/Delta/101.dll”. (Citation: Dragos CRASHOVERRIDE Oct 2018)
G0034 | Sandworm Team | group | uses | Masquerading | technique | [Sandworm Team](https://collaborate.mitre.org/attackics/index.php/Group/G0007) transfers executable files as .txt. and then renames them to .exe, likely to avoid detection through extension tracking. (Citation: Dragos CRASHOVERRIDE Oct 2018)
G0034 | Sandworm Team | group | uses | Remote Services | technique | [Sandworm Team](https://collaborate.mitre.org/attackics/index.php/Group/G0007) appears to use MS-SQL access to a pivot machine, allowing code execution throughout the ICS network. (Citation: Dragos CRASHOVERRIDE Oct 2018)
G0034 | Sandworm Team | group | uses | Remote Services | technique | In the Ukraine 2015 Incident, [Sandworm Team](https://collaborate.mitre.org/attackics/index.php/Group/G0007) used native remote access tools to directly interface with operator workstations and control ICS components.(Citation: ICS SANS Ukraine March 2018)
G0034 | Sandworm Team | group | uses | Scripting | technique | [Sandworm Team](https://collaborate.mitre.org/attackics/index.php/Group/G0007) Sandworm Team utilized VBS and batch scripts for file movement and as wrappers for PowerShell execution. (Citation: Dragos CRASHOVERRIDE Oct 2018)
G0034 | Sandworm Team | group | uses | Spearphishing Attachment | technique | In the Ukraine 2015 Incident, [Sandworm Team](https://collaborate.mitre.org/attackics/index.php/Group/G0007) sent spearphishing attachments to three energy distribution companies containing malware to gain access to victim systems.(Citation: DOJ Sandworm Team October 2020)
G0034 | Sandworm Team | group | uses | System Firmware | technique | In the Ukraine 2015 Incident, [Sandworm Team](https://collaborate.mitre.org/attackics/index.php/Group/G0007) developed and used malicious firmware to render communication devices inoperable.(Citation: ICS SANS Ukraine March 2018)
G0034 | Sandworm Team | group | uses | Unauthorized Command Message | technique | In the Ukraine 2015 Incident, [Sandworm Team](https://collaborate.mitre.org/attackics/index.php/Group/G0007) issued unauthorized commands to substation breakers after gaining control of operator workstations and accessing a distribution management system (DMS) client application.(Citation: ICS SANS Ukraine March 2018)
G0034 | Sandworm Team | group | uses | Valid Accounts | technique | [Sandworm Team](https://collaborate.mitre.org/attackics/index.php/Group/G0007) used valid accounts to laterally move through VPN connections and dual-homed systems.(Citation: Dragos Electrum)(Citation: Dragos CRASHOVERRIDE) In the Ukraine 2015 Incident, Sandworm Team blocked command messages by using malicious firmware to render communication devices inoperable.(Citation: ICS SANS Ukraine March 2018)
G0088 | TEMP.Veles | group | uses | Drive-by Compromise | technique | [XENOTIME](https://collaborate.mitre.org/attackics/index.php/Group/G0001) utilizes watering hole websites to target industrial employees.(Citation: CyberScoop Xenotime May 2018)
G0088 | TEMP.Veles | group | uses | External Remote Services | technique | [XENOTIME](https://collaborate.mitre.org/attackics/index.php/Group/G0001) utilized remote desktop protocol (RDP) jump boxes to move into the ICS environment.(Citation: Dragos TRISIS Dec 2017)
G0088 | TEMP.Veles | group | uses | Remote Services | technique | [XENOTIME](https://collaborate.mitre.org/attackics/index.php/Group/G0001) utilized remote desktop protocol (RDP) jump boxes to move into the ICS environment.(Citation: Dragos TRISIS December 2017
G0088 | TEMP.Veles | group | uses | Supply Chain Compromise | technique | [XENOTIME](https://collaborate.mitre.org/attackics/index.php/Group/G0001) targeted several ICS vendors and manufacturers.(Citation: Dragos Aug 2019)
G0088 | TEMP.Veles | group | uses | Valid Accounts | technique | [XENOTIME](https://collaborate.mitre.org/attackics/index.php/Group/G0001) used valid credentials when laterally moving through RDP jump boxes into the ICS environment.(Citation: Dragos TRISIS Dec 2017)
| ACAD/Medre.A | software | uses | Data from Information Repositories | technique | [ACAD/Medre.A](https://collaborate.mitre.org/attackics/index.php/Software/S0018) collects information related to the AutoCAD application. The worm collects AutoCAD (*.dwg) files with drawings from information repositories.
| ACAD/Medre.A | software | uses | Theft of Operational Information | technique | [ACAD/Medre.A](https://collaborate.mitre.org/attackics/index.php/Software/S0018) can collect AutoCad files with drawings. These drawings may contain operational information.
S0093 | Backdoor.Oldrea | software | uses | Automated Collection | technique | Using OPC, a component of [Backdoor.Oldrea](https://collaborate.mitre.org/attackics/index.php/Software/S0003) gathers any details about connected devices and sends them back to the C2 for the attackers to analyze.(Citation: F-Secure Labs Jun 2014)
S0093 | Backdoor.Oldrea | software | uses | Denial of Service | technique | The [Backdoor.Oldrea](https://collaborate.mitre.org/attackics/index.php/Software/S0003) payload has caused multiple common OPC platforms to intermittently crash. This could cause a denial of service effect on applications reliant on OPC communications.(Citation: CISA Advisory (ICSA-14-178-01))
S0093 | Backdoor.Oldrea | software | uses | Point & Tag Identification | technique | [Backdoor.Oldrea](https://collaborate.mitre.org/attackics/index.php/Software/S0003) enumerates all OPC tags and queries for specific fields such as server state, tag name, type, access, and id.(Citation: FireEye Havex Jul 2014)
S0093 | Backdoor.Oldrea | software | uses | Point & Tag Identification | technique | The [Backdoor.Oldrea](https://collaborate.mitre.org/attackics/index.php/Software/S0003) payload has the capability of enumerating OPC tags, in addition to more generic OPC server information. The server data and tag names can provide information about the names and function of control devices.(Citation: ICS-CERT ICSA-14-178-01 August 2018)(Citation: F-Secure Havex June 2014)
S0093 | Backdoor.Oldrea | software | uses | Remote System Discovery | technique | The [Backdoor.Oldrea](https://collaborate.mitre.org/attackics/index.php/Software/S0003) ICS malware plugin relies on Windows networking (WNet) to discover all the servers, including OPC servers, that are reachable by the compromised machine over the network.(Citation: SemanticScholar Dec 2015)
S0093 | Backdoor.Oldrea | software | uses | Remote System Information Discovery | technique | [Backdoor.Oldrea](https://collaborate.mitre.org/attackics/index.php/Software/S0003) payload gathers server information that includes CLSID, server name, Program ID, OPC version, vendor information, running state, group count, and server bandwidth. This information helps indicate the role the server has in the control process.(Citation: ICS-CERT ICSA-14-178-01 August 2018)(Citation: F-Secure Havex June 2014)
S0093 | Backdoor.Oldrea | software | uses | Spearphishing Attachment | technique | The [Backdoor.Oldrea](https://collaborate.mitre.org/attackics/index.php/Software/S0003) RAT is distributed through a trojanized installer attached to emails.(Citation: F-Secure Labs Jun 2014)
S0093 | Backdoor.Oldrea | software | uses | Supply Chain Compromise | technique | The [Backdoor.Oldrea](https://collaborate.mitre.org/attackics/index.php/Software/S0003) RAT is distributed through trojanized installers planted on compromised vendor sites.(Citation: F-Secure Labs Jun 2014)
S0093 | Backdoor.Oldrea | software | uses | User Execution | technique | Execution of [Backdoor.Oldrea](https://collaborate.mitre.org/attackics/index.php/Software/S0003) relies on a user opening a trojanized installer attached to an email.(Citation: F-Secure Labs Jun 2014)(Citation: ICS Malware: Havex and Black Energy)
S0606 | Bad Rabbit | software | uses | Drive-by Compromise | technique | [Bad Rabbit](https://collaborate.mitre.org/attackics/index.php/Software/S0005) ransomware spreads through drive-by attacks where insecure websites are compromised. While the target is visiting a legitimate website, a malware dropper is being downloaded from the threat actor’s infrastructure.(Citation: Kaspersky Bad Rabbit Oct 2017)
S0606 | Bad Rabbit | software | uses | Exploitation of Remote Services | technique | [Bad Rabbit](https://collaborate.mitre.org/attackics/index.php/Software/S0005) initially infected IT networks, but by means of an exploit (particularly the SMBv1-targeting MS17-010 vulnerability) spread to industrial networks.(Citation: Dragos Apr 2019)
S0606 | Bad Rabbit | software | uses | External Remote Services | technique | [Bad Rabbit](https://collaborate.mitre.org/attackics/index.php/Software/S0005) can utilize exposed SMB services to access industrial networks.(Citation: Dragos Apr 2019)
S0606 | Bad Rabbit | software | uses | Lateral Tool Transfer | technique | [Bad Rabbit](https://collaborate.mitre.org/attackics/index.php/Software/S0005) can move laterally through industrial networks by means of the SMB service.(Citation: Dragos Apr 2019)
S0606 | Bad Rabbit | software | uses | Loss of Productivity and Revenue | technique | Several transportation organizations in Ukraine have suffered from being infected by [Bad Rabbit](https://collaborate.mitre.org/attackics/index.php/Software/S0005), resulting in some computers becoming encrypted, according to media reports. (Citation: ESET Bad Rabbit Oct 2017)
S0606 | Bad Rabbit | software | uses | User Execution | technique | [Bad Rabbit](https://collaborate.mitre.org/attackics/index.php/Software/S0005) is disguised as an Adobe Flash installer. When the file is opened it starts locking the infected computer.(Citation: Kaspersky Bad Rabbit Oct 2017)
S0089 | BlackEnergy | software | uses | Spearphishing Attachment | technique | [BlackEnergy 3](https://collaborate.mitre.org/attackics/index.php/Software/S0004) targeted energy sector organizations in a wide reaching email spearphishing campaign. Adversaries utilized malicious Microsoft Word documents attachments.(Citation: Booz Allen Hamilton)
S0089 | BlackEnergy | software | uses | Standard Application Layer Protocol | technique | [BlackEnergy 3](https://collaborate.mitre.org/attackics/index.php/Software/S0004) uses HTTP POST request to contact external command and control servers.(Citation: Booz Allen Hamilton)
S0089 | BlackEnergy | software | uses | Valid Accounts | technique | [BlackEnergy 3](https://collaborate.mitre.org/attackics/index.php/Software/S0004) utilizes valid user and administrator credentials, in addition to creating new administrator accounts to maintain presence.(Citation: Booz Allen Hamilton)
S0608 | Conficker | software | uses | Loss of Availability | technique | A [Conficker](https://collaborate.mitre.org/attackics/index.php/Software/S0012) infection at a nuclear power plant forced the facility to temporarily shutdown.(Citation: Softpedia News Apr 2016)
S0608 | Conficker | software | uses | Loss of Productivity and Revenue | technique | A [Conficker](https://collaborate.mitre.org/attackics/index.php/Software/S0012) infection at a nuclear power plant forced the facility to shutdown and go through security procedures involved with such events, with its staff scanning computer systems and going through all the regular checks and motions before putting the plant back into production.(Citation: Softpedia News Apr 2016)
S0608 | Conficker | software | uses | Replication Through Removable Media | technique | [Conficker](https://collaborate.mitre.org/attackics/index.php/Software/S0012) exploits Windows drive shares. Once it has infected a computer, Conficker automatically copies itself to all visible open drive shares on other computers inside the network.(Citation: Symantec Conficker Jun 20) Nuclear power plant officials suspect someone brought in Conficker by accident on a USB thumb drive, either from home or computers found in the power plant's facility.(Citation: Softpedia News Apr 2016)
S0038 | Duqu | software | uses | Data from Information Repositories | technique | [Duqu](https://collaborate.mitre.org/attackics/index.php/Software/S0014)'s purpose is to 'gather intelligence data and assets from entities such as industrial infrastructure and system manufacturers, amongst others not in the industrial sector, in order to more easily conduct a future attack against another third party.'(Citation: Symantec W.32 Duqu)
S0038 | Duqu | software | uses | Theft of Operational Information | technique | [Duqu](https://collaborate.mitre.org/attackics/index.php/Software/S0014)downloads additional modules for the collection of data in information repositories. The modules are named: infostealer 1, infostealer 2 and reconnaissance.(Citation: Symantec W.32 Duqu)
S0605 | EKANS | software | uses | Loss of Productivity and Revenue | technique | [EKANS](https://collaborate.mitre.org/attackics/index.php/Software/S0014) infection resulted in a temporary production loss within a Honda manufacturing plant.(Citation: Forbes Snake Ransomware June 2020)
S0605 | EKANS | software | uses | Masquerading | technique | [EKANS](https://collaborate.mitre.org/attackics/index.php/Software/S0014) masquerades itself as a valid executable with the filename 'update.exe'. Many valid programs use the process name 'update.exe' to perform background software updates.(Citation: Dragos EKANS February 2020)
S0605 | EKANS | software | uses | Network Connection Enumeration | technique | [EKANS](https://collaborate.mitre.org/attackics/index.php/Software/S0014) performs a DNS lookup of an internal domain name associated with its target network to identify if it was deployed on the intended system.(Citation: Fortinet EKANS July 2020)
S0605 | EKANS | software | uses | Service Stop | technique | Before encrypting the process, [EKANS](https://collaborate.mitre.org/attackics/index.php/Software/S0014) first kills the process if its name matches one of the processes defined on the kill-list.(Citation: FireEye Ransomware Against the Machine July 2020)(Citation: FireEye OT Ransomware July 2020) EKANS also utilizes netsh commands to implement firewall rules that blocks any remote communication with the device.(Citation: Fortinet EKANS July 2020)
S0143 | Flame | software | uses | Data from Information Repositories | technique | [Flame](https://collaborate.mitre.org/attackics/index.php/Software/S0015) has built-in modules to gather information from compromised computers.(Citation: Symantec W32.Flamer)
S0143 | Flame | software | uses | Theft of Operational Information | technique | [Flame](https://collaborate.mitre.org/attackics/index.php/Software/S0015) can collect AutoCAD design data and visio diagrams as well as other documents that may contain operational information.(Citation: Symantec W32.Flamer)
S0604 | Industroyer | software | uses | Activate Firmware Update Mode | technique | The [Industroyer](https://collaborate.mitre.org/attackics/index.php/Software/S0001) SPIROTEC DoS module places the victim device into 'firmware update' mode. This is a legitimate use case under normal circumstances, but in this case is used the adversary to prevent the SPIROTEC from performing its designed protective functions. As a result the normal safeguards are disabled, leaving an unprotected link in the electric transmission.(Citation: Dragos CRASHOVERRIDE Aug 2019)
S0604 | Industroyer | software | uses | Automated Collection | technique | [Industroyer](https://collaborate.mitre.org/attackics/index.php/Software/S0001), automatically collects protocol object data to learn about control devices in the environment.(Citation: ESET Win32/Industroyer Jun 2017)
S0604 | Industroyer | software | uses | Block Command Message | technique | In [Industroyer](https://collaborate.mitre.org/attackics/index.php/Software/S0001), the first COM port from the configuration file is used for the actual communication and the two other COM ports are just opened to prevent other processes accessing them. Thus, the IEC 101 payload component is able to take over and maintain control of the RTU device.(Citation: ESET Win32/Industroyer Jun 2017)
S0604 | Industroyer | software | uses | Block Reporting Message | technique | [Industroyer](https://collaborate.mitre.org/attackics/index.php/Software/S0001) uses the first COM port from the configuration file for the communication and the other two COM ports are opened to prevent other processes accessing them. This may block processes or operators from getting reporting messages from a device.(Citation: ESET Win32/Industroyer Jun 2017)
S0604 | Industroyer | software | uses | Block Serial COM | technique | In [Industroyer](https://collaborate.mitre.org/attackics/index.php/Software/S0001), the first COM port from the configuration file is used for the actual communication and the two other COM ports are just opened to prevent other processes accessing them. Thus, the IEC 101 payload component is able to take over and maintain control of the RTU device.(Citation: ESET Win32/Industroyer Jun 2017)
S0604 | Industroyer | software | uses | Brute Force I/O | technique | The [Industroyer](https://collaborate.mitre.org/attackics/index.php/Software/S0001), IEC 104 module has 3 modes available to perform its attack. These modes are range, shift, and sequence. The range mode operates in 2 stages. The first stage of range mode gathers Information Object Addresses (IOA) and sends 'select and execute' packets to switch the state. The second stage of range mode has an infinite loop where it will switch the state of all of the previously discovered IOAs. Shift mode is similar to range mode, but instead of staying within the same range, it will add a shift value to the default range values.(Citation: ESET Win32/Industroyer Jun 2017)
S0604 | Industroyer | software | uses | Command-Line Interface | technique | The name of the [Industroyer](https://collaborate.mitre.org/attackics/index.php/Software/S0001) payload DLL is supplied by the attackers via a command line parameter supplied in one of the main backdoor’s 'execute a shell command' commands.(Citation: ESET Win32/Industroyer Jun 2017)
S0604 | Industroyer | software | uses | Connection Proxy | technique | In [Industroyer](https://collaborate.mitre.org/attackics/index.php/Software/S0001), Industroyer attempts to connect with a hardcoded internal proxy on TCP 3128 [default Squid proxy]. If established, the backdoor attempts to reach an external C2 server via the internal proxy.
S0604 | Industroyer | software | uses | Data Destruction | technique | [Industroyer](https://collaborate.mitre.org/attackics/index.php/Software/S0001), has a destructive wiper that 'overwrites all ICS configuration files across the hard drives and all mapped network drives specifically targeting ABB PCM600 configuration files'.(Citation: Dragos Industroyer Jun 2017)
S0604 | Industroyer | software | uses | Denial of Control | technique | [Industroyer](https://collaborate.mitre.org/attackics/index.php/Software/S0001) is able to block serial COM channels temporarily causing a denial of control.(Citation: ESET Win32/Industroyer Jun 2017)
S0604 | Industroyer | software | uses | Denial of Service | technique | The [Industroyer](https://collaborate.mitre.org/attackics/index.php/Software/S0001), SIPROTEC DoS module exploits the CVE-2015-5374 vulnerability in order to render a Siemens SIPROTEC device unresponsive. Once this vulnerability is successfully exploited, the target device stops responding to any commands until it is rebooted manually.(Citation: ESET Win32/Industroyer Jun 2017)Once the tool is executed it sends specifically crafted packets to port 50,000 of the target IP addresses using UDP. The UDP packet contains the following 18 byte payload: 0x11 49 00 00 00 00 00 00 00 00 00 00 00 00 00 00 28 9E.(Citation: ESET Win32/Industroyer Jun 2017)
S0604 | Industroyer | software | uses | Denial of View | technique | [Industroyer](https://collaborate.mitre.org/attackics/index.php/Software/S0001) is able to block serial COM channels temporarily causing a denial of view.(Citation: ESET Win32/Industroyer Jun 2017)
S0604 | Industroyer | software | uses | Device Restart/Shutdown | technique | The [Industroyer](https://collaborate.mitre.org/attackics/index.php/Software/S0001), SIPROTEC DoS module exploits the CVE-2015-5374 vulnerability in order to render a Siemens SIPROTEC device unresponsive. Once this vulnerability is successfully exploited, the target device stops responding to any commands until it is rebooted manually.(Citation: ESET Win32/Industroyer Jun 2017)Once the tool is executed it sends specifically crafted packets to port 50,000 of the target IP addresses using UDP. The UDP packet contains the following 18 byte payload: 0x11 49 00 00 00 00 00 00 00 00 00 00 00 00 00 00 28 9E.(Citation: ESET Win32/Industroyer Jun 2017)
S0604 | Industroyer | software | uses | Loss of Control | technique | [Industroyer](https://collaborate.mitre.org/attackics/index.php/Software/S0001)'s data wiper component removes the registry 'image path' throughout the system and overwrites all files, rendering the system unusable.(Citation: ESET Win32/Industroyer Jun 2017)
S0604 | Industroyer | software | uses | Loss of Protection | technique | [Industroyer](https://collaborate.mitre.org/attackics/index.php/Software/S0001)contained a module which leveraged a vulnerability in the Siemens SIPROTEC relays (CVE-2015-5374) to create a Denial of Service against automated protective relays.(Citation: Dragos CRASHOVERRIDE October 2018)
S0604 | Industroyer | software | uses | Loss of Safety | technique | [Industroyer](https://collaborate.mitre.org/attackics/index.php/Software/S0001)contained a module which leveraged a vulnerability in the Siemens SIPROTEC relays (CVE-2015-5374) to create a Denial of Service against automated protective relays.(Citation: Dragos CRASHOVERRIDE Oct 2018)
S0604 | Industroyer | software | uses | Loss of View | technique | [Industroyer](https://collaborate.mitre.org/attackics/index.php/Software/S0001)'s data wiper component removes the registry 'image path' throughout the system and overwrites all files, rendering the system unusable.(Citation: ESET Win32/Industroyer Jun 2017)
S0604 | Industroyer | software | uses | Manipulation of Control | technique | [Industroyer](https://collaborate.mitre.org/attackics/index.php/Software/S0001) toggles breakers to the open state utilizing unauthorized command messages.(Citation: ESET Win32/Industroyer Jun 2017)
S0604 | Industroyer | software | uses | Manipulation of View | technique | [Industroyer](https://collaborate.mitre.org/attackics/index.php/Software/S0001)'s OPC module can brute force values and will send out a 0x01 status which for the target systems equates to a 'Primary Variable Out of Limits' misdirecting operators from understanding protective relay status.(Citation: ESET Win32/Industroyer Jun 2017)
S0604 | Industroyer | software | uses | Masquerading | technique | [Industroyer](https://collaborate.mitre.org/attackics/index.php/Software/S0001), modules operate by inhibiting the normal SCADA master communication functions and then activate a replacement master communication module managed by the malware, which executes a script of commands to issue normal protocol messages.(Citation: ESET Win32/Industroyer Jun 2017)
S0604 | Industroyer | software | uses | Network Connection Enumeration | technique | [Industroyer](https://collaborate.mitre.org/attackics/index.php/Software/S0001), contains an IEC 61850 module that enumerates all connected network adapters to determine their TCP/IP subnet masks.(Citation: ESET Win32/Industroyer Jun 2017)
S0604 | Industroyer | software | uses | Remote System Discovery | technique | The [Industroyer](https://collaborate.mitre.org/attackics/index.php/Software/S0001), IEC 61850 payload enumerates all possible IP addresses for each of the subnet masks for the interfaces on the infected machine, and tries to connect to port 102 on each of those addresses. Therefore, this component has the ability to discover relevant devices in the network automatically.(Citation: ESET Win32/Industroyer Jun 2017)
S0604 | Industroyer | software | uses | Remote System Information Discovery | technique | The [Industroyer](https://collaborate.mitre.org/attackics/index.php/Software/S0001) IEC 61850 component sends the domain-specific MMS getNameList request to determine what logical nodes the device supports. It then searches the logical nodes for the “CSW” value, which indicates the device performs a circuit breaker or switch control function.(Citation: ESET Win32/Industroyer June 2017)
S0604 | Industroyer | software | uses | Remote System Information Discovery | technique | [Industroyer](https://collaborate.mitre.org/attackics/index.php/Software/S0001) s OPC DA module also uses IOPCBrowseServerAddressSpace to look for items with the following strings: 'ctlSelOn', 'ctlOperOn', 'ctlSelOff', 'ctlOperOff', 'Pos and stVal'.(Citation: ESET Win32/Industroyer June 2017)
S0604 | Industroyer | software | uses | Remote System Information Discovery | technique | [Industroyer](https://collaborate.mitre.org/attackics/index.php/Software/S0001) IEC 60870-5-104 module includes a range mode to discover Information Object Addresses (IOAs) by enumerating through each.(Citation: ESET Win32/Industroyer June 2017)
S0604 | Industroyer | software | uses | Service Stop | technique | [Industroyer](https://collaborate.mitre.org/attackics/index.php/Software/S0001) has the capability to stop a service itself, or to login as a user and stop a service as that user.(Citation: ESET Win32/Industroyer Jun 2017)
S0604 | Industroyer | software | uses | Unauthorized Command Message | technique | [Industroyer](https://collaborate.mitre.org/attackics/index.php/Software/S0001) Using its protocol payloads, Industroyer sends unauthorized commands to RTUs to change the state of equipment.(Citation: ESET Win32/Industroyer Jun 2017)
S0607 | KillDisk | software | uses | Data Destruction | technique | [KillDisk](https://collaborate.mitre.org/attackics/index.php/Software/S0016) is able to delete system files to make the system unbootable and targets 35 different types of files for deletion.(Citation: ESET BlackEnergy)
S0607 | KillDisk | software | uses | Indicator Removal on Host | technique | [KillDisk](https://collaborate.mitre.org/attackics/index.php/Software/S0016) deletes application, security, setup, and system event logs from Windows systems.(Citation: ESET BlackEnergy)
S0607 | KillDisk | software | uses | Loss of View | technique | [KillDisk](https://collaborate.mitre.org/attackics/index.php/Software/S0016) erases the master boot record (MBR) and system logs, leaving the system unusable.(Citation: Booz Allen Hamilton)
S0607 | KillDisk | software | uses | Service Stop | technique | [KillDisk](https://collaborate.mitre.org/attackics/index.php/Software/S0016) looks for and terminates two non-standard processes, one of which is an ICS application.(Citation: ESET BlackEnergy)
S0372 | LockerGoga | software | uses | Loss of Control | technique | Some of Norsk Hydro's production systems were impacted by a [LockerGoga](https://collaborate.mitre.org/attackics/index.php/Software/S0008) infection. This resulted in a loss of control which forced the company to switch to manual operations.(Citation: DoublePulsar LockerGoga)(Citation: Hydro)
S0372 | LockerGoga | software | uses | Loss of Productivity and Revenue | technique | While Norsk Hydro attempted to recover from a [LockerGoga](https://collaborate.mitre.org/attackics/index.php/Software/S0008) infection, most of its 160 manufacturing locations switched to manual (non-IT driven) operations. Manual operations can result in a loss of productivity.(Citation: DoublePulsar LockerGoga)(Citation: Hydro)
S0372 | LockerGoga | software | uses | Loss of View | technique | Some of Norsk Hydro's production systems were impacted by a [LockerGoga](https://collaborate.mitre.org/attackics/index.php/Software/S0008) infection. This resulted in a loss of view which forced the company to switch to manual operations.(Citation: DoublePulsar LockerGoga)(Citation: Hydro)
S0368 | NotPetya | software | uses | Exploitation of Remote Services | technique | [NotPetya](https://collaborate.mitre.org/attackics/index.php/Software/S0006) initially infected IT networks, but by means of an exploit (particularly the SMBv1-targeting MS17-010 vulnerability) spread to industrial networks.(Citation: Dragos Apr 2019)
S0368 | NotPetya | software | uses | External Remote Services | technique | [NotPetya](https://collaborate.mitre.org/attackics/index.php/Software/S0006) can utilize exposed SMB services to access industrial networks.(Citation: Dragos Apr 2019)
S0368 | NotPetya | software | uses | Lateral Tool Transfer | technique | [NotPetya](https://collaborate.mitre.org/attackics/index.php/Software/S0006) can move laterally through industrial networks by means of the SMB service.(Citation: Dragos Apr 2019)
S0368 | NotPetya | software | uses | Loss of Productivity and Revenue | technique | [NotPetya](https://collaborate.mitre.org/attackics/index.php/Software/S0006) disrupted manufacturing facilities supplying vaccines, resulting in a halt of production and the inability to meet demand for specific vaccines.(Citation: Bloomberg Dec 2019)
| PLC-Blaster | software | uses | Change Operating Mode | technique | [PLC-Blaster](https://collaborate.mitre.org/attackics/index.php/Software/S0009) stops the execution of the user program on the target to enable the transfer of its own code. The worm then copies itself to the target and subsequently starts the target PLC again.(Citation: BlackHat Mar 2016)
| PLC-Blaster | software | uses | Denial of Service | technique | The execution on the PLC can be stopped by violating the cycle time limit. The [PLC-Blaster](https://collaborate.mitre.org/attackics/index.php/Software/S0009) implements an endless loop triggering an error condition within the PLC with the impact of a DoS.(Citation: BlackHat Mar 2016)
| PLC-Blaster | software | uses | Execution through API | technique | [PLC-Blaster](https://collaborate.mitre.org/attackics/index.php/Software/S0009) utilizes the PLC communication and management API to load executable Program Organization Units.(Citation: BlackHat Mar 2016)
| PLC-Blaster | software | uses | Manipulate I/O Image | technique | [PLC-Blaster](https://collaborate.mitre.org/attackics/index.php/Software/S0009) may manipulate any outputs of the PLC. Using the POU POKE any value within the process image may be modified.(Citation: BlackHat Mar 2016)
| PLC-Blaster | software | uses | Modify Controller Tasking | technique | [PLC-Blaster](https://collaborate.mitre.org/attackics/index.php/Software/S0009) adds to the user program already running on the target PLC. An additional OB, OB9999. The original code on the target is untouched. The OB is automatically detected by the PLC and executed.(Citation: BlackHat Mar 2016)
| PLC-Blaster | software | uses | Modify Program | technique | [PLC-Blaster](https://collaborate.mitre.org/attackics/index.php/Software/S0009) copies itself to various Program Organization Units (POU) on the target device. The POUs include the Data Block, Function, and Function Block.(Citation: BlackHat Mar 2016)
| PLC-Blaster | software | uses | Native API | technique | [PLC-Blaster](https://collaborate.mitre.org/attackics/index.php/Software/S0009) uses the system function blocks TCON and TDISCON to initiate and destroy TCP connections to arbitrary systems. Buffers may be sent and received on these connections with TRCV und TSEND system function blocks.(Citation: BlackHat Mar 2016)
| PLC-Blaster | software | uses | Program Download | technique | [PLC-Blaster](https://collaborate.mitre.org/attackics/index.php/Software/S0009) utilizes the PLC communication and management API to load executable Program Organization Units.(Citation: BlackHat Mar 2016)
| PLC-Blaster | software | uses | Remote System Discovery | technique | [PLC-Blaster](https://collaborate.mitre.org/attackics/index.php/Software/S0009) scans the network to find other Siemens S7 PLC devices to infect. It locates these devices by checking for a service listening on TCP port 102.(Citation: BlackHat Mar 2016)
S0496 | REvil | software | uses | Loss of Productivity and Revenue | technique | The [REvil](https://collaborate.mitre.org/attackics/index.php/Software/S0019) malware gained access to an organization’s network and encrypted sensitive files used by OT equipment.(Citation: Dragos Ransomware in ICS Environments Dec 2020)
S0496 | REvil | software | uses | Masquerading | technique | [REvil](https://collaborate.mitre.org/attackics/index.php/Software/S0019) searches for whether the Ahnlab 'autoup.exe' service is running on the target system and injects its payload into this existing process.(Citation: Cybereason Sodinokibi August 2019)
S0496 | REvil | software | uses | Remote Services | technique | [REvil](https://collaborate.mitre.org/attackics/index.php/Software/S0019) uses the SMB protocol to encrypt files located on remotely connected file shares.(Citation: Darktrace Sodinokibi Feb 2020)
S0496 | REvil | software | uses | Scripting | technique | [REvil](https://collaborate.mitre.org/attackics/index.php/Software/S0019) utilizes JavaScript, WScript, and PowerShell scripts to execute. The malicious JavaScript attachment has an obfuscated PowerShell script that executes the malware.(Citation: Cybereason Sodinokibi August 2019)
S0496 | REvil | software | uses | Service Stop | technique | [REvil](https://collaborate.mitre.org/attackics/index.php/Software/S0019) searches for all processes listed in the “prc” field within its configuration file and then terminates each process.(Citation: McAfee Sodinokibi October 2019)
S0496 | REvil | software | uses | Standard Application Layer Protocol | technique | [REvil](https://collaborate.mitre.org/attackics/index.php/Software/S0019) sends HTTPS POST messages with randomly generated URLs to communicate with a remote server.(Citation: Cybereason Sodinokibi August 2019)(Citation: SecureWorks REvil/Sodinokibi 2019)
S0496 | REvil | software | uses | Theft of Operational Information | technique | [REvil](https://collaborate.mitre.org/attackics/index.php/Software/S0019) sends exfiltrated data from the victim’s system using HTTPS POST messages sent to the C2 system.(Citation: McAfee Sodinokibi October 2019)
S0496 | REvil | software | uses | User Execution | technique | [REvil](https://collaborate.mitre.org/attackics/index.php/Software/S0019) initially executes when the user clicks on a JavaScript file included in the phishing email’s .zip attachment.(Citation: Cybereason Sodinokibi August 2019)
S0446 | Ryuk | software | uses | Loss of Productivity and Revenue | technique | An enterprise resource planning (ERP) manufacturing server was lost to the [Ryuk](https://collaborate.mitre.org/attackics/index.php/Software/S0011) attack. The manufacturing process had to rely on paper and existing orders to keep the shop floor open.(Citation: DarkReading)
S0603 | Stuxnet | software | uses | Command-Line Interface | technique | [Stuxnet](https://collaborate.mitre.org/attackics/index.php/Software/S0010) will store and execute SQL code that will extract and execute Stuxnet from the saved CAB file using xp_cmdshell with the following command: set @s = ’master..xp _ cmdshell ‘’extrac32 /y “‘+@t+‘” “’+@t+‘x”‘’’; exec(@s);(Citation: Wired W32.Stuxnet Feb 2011)
S0603 | Stuxnet | software | uses | Commonly Used Port | technique | [Stuxnet](https://collaborate.mitre.org/attackics/index.php/Software/S0010) attempts to contact command and control servers on port 80 to send basic information about the computer it has compromised.(Citation: Wired W32.Stuxnet Feb 2011)
S0603 | Stuxnet | software | uses | Damage to Property | technique | [Stuxnet](https://collaborate.mitre.org/attackics/index.php/Software/S0010) attacks were designed to over-pressure and damage centrifuge rotors by manipulating process pressure and rotor speeds over time. One focused on a routine to change centrifuge rotor speeds, while the other manipulated critical resonance speeds to over-pressure them.(Citation: Langner Nov 2013)
S0603 | Stuxnet | software | uses | Execution through API | technique | [Stuxnet](https://collaborate.mitre.org/attackics/index.php/Software/S0010) utilizes the PLC communication and management API to load executable [Program Organization Units](https://collaborate.mitre.org/attackics/index.php/Technique/T844).(Citation: Wired W32.Stuxnet Feb 2011)
S0603 | Stuxnet | software | uses | Hooking | technique | [Stuxnet](https://collaborate.mitre.org/attackics/index.php/Software/S0010) modifies the Import Address Tables DLLs to hook specific APIs that are used to open project files.(Citation: Wired W32.Stuxnet Feb 2011)
S0603 | Stuxnet | software | uses | I/O Image | technique | [Stuxnet](https://collaborate.mitre.org/attackics/index.php/Software/S0010) copies the input area of an I/O image into data blocks with a one second interval between copies, forming a 21 second recording of the input area. The input area contains information being passed to the PLC from a peripheral. For example, the current state of a valve or the temperature of a device.(Citation: Wired W32.Stuxnet Feb 2011)
S0603 | Stuxnet | software | uses | Lateral Tool Transfer | technique | [Stuxnet](https://collaborate.mitre.org/attackics/index.php/Software/S0010) sends an SQL statement that creates a table and inserts a binary value into the table. The binary value is a hex string representation of the main Stuxnet DLL as an executable file (formed using resource 210) and an updated configuration data block.(Citation: Wired W32.Stuxnet Feb 2011)
S0603 | Stuxnet | software | uses | Manipulate I/O Image | technique | When the peripheral output is written to, sequence C intercepts the output and ensures it is not written to the process image output. The output is the instructions the PLC sends to a device to change its operating behavior. By intercepting the peripheral output, [Stuxnet](https://collaborate.mitre.org/attackics/index.php/Software/S0010) prevents an operator from noticing unauthorized commands sent to the peripheral.(Citation: Wired W32.Stuxnet Feb 2011)
S0603 | Stuxnet | software | uses | Manipulation of Control | technique | [Stuxnet](https://collaborate.mitre.org/attackics/index.php/Software/S0010) can reprogram a PLC and change critical parameters in such a way that legitimate commands can be overridden or intercepted. In addition, [Stuxnet](https://collaborate.mitre.org/attackics/index.php/Software/S0010#scite-b3a32e169ec1545f620839e1471333e0) can apply inappropriate command sequences or parameters to cause damage to property.
S0603 | Stuxnet | software | uses | Manipulation of View | technique | [Stuxnet](https://collaborate.mitre.org/attackics/index.php/Software/S0010) manipulates the view of operators replaying process input and manipulating the I/O image to evade detection and inhibit protection functions.(Citation: Langner Nov 2013)(Citation: Wired W32.Stuxnet Feb 2011)
S0603 | Stuxnet | software | uses | Masquerading | technique | [Stuxnet](https://collaborate.mitre.org/attackics/index.php/Software/S0010) renames a dll responsible for handling communications with a PLC. It replaces the original .dll file with its own version that allows it to intercept any calls that are made to access the PLC.(Citation: Wired W32.Stuxnet Feb 2011)
S0603 | Stuxnet | software | uses | Modify Controller Tasking | technique | [Stuxnet](https://collaborate.mitre.org/attackics/index.php/Software/S0010) infects OB1 so that the its malicious code sequence is executed at the start of a cycle. It also infects OB35. OB35 acts as a watchdog, and on certain conditions, it can stop the execution of OB1.(Citation: Wired W32.Stuxnet Feb 2011)
S0603 | Stuxnet | software | uses | Modify Parameter | technique | In states 3 and 4 [Stuxnet](https://collaborate.mitre.org/attackics/index.php/Software/S0010) sends two network bursts (done through the DP_SEND primitive). The data in the frames are instructions for the frequency converter drives. For example one of the frames contains records that change the maximum frequency (the speed at which the motor will operate). The frequency converter drives consist of parameters, which can be remotely configured via Profibus. One can write new values to these parameters changing the behavior of the device.(Citation: Wired W32.Stuxnet Feb 2011)
S0603 | Stuxnet | software | uses | Modify Program | technique | [Stuxnet](https://collaborate.mitre.org/attackics/index.php/Software/S0010) infects PLCs with different code depending on the characteristics of the target system. An infection sequence consists of code blocks and data blocks that will be downloaded to the PLC to alter its behavior.(Citation: Wired W32.Stuxnet Feb 2011)
S0603 | Stuxnet | software | uses | Monitor Process State | technique | [Stuxnet](https://collaborate.mitre.org/attackics/index.php/Software/S0010) examines fields recorded by the DP_RECV monitor to determine if the target system is in a particular state of operation.(Citation: Wired W32.Stuxnet Feb 2011)
S0603 | Stuxnet | software | uses | Native API | technique | [Stuxnet](https://collaborate.mitre.org/attackics/index.php/Software/S0010) calls system function blocks which are part of the operating system running on the PLC. They’re used to execute system tasks, such as reading the system clock (SFC1) and generating data blocks on the fly.(Citation: Wired W32.Stuxnet Feb 2011)
S0603 | Stuxnet | software | uses | Network Sniffing | technique | DP_RECV is the name of a standard function block used by network coprocessors. It is used to receive network frames on the Profibus – a standard industrial network bus used for distributed I/O. The original block is copied to FC1869, and then replaced by a malicious block. Each time the function is used to receive a packet, the malicious Stuxnet block takes control: it will call the original DP_RECV in FC1869 and then perform postprocessing on the packet data. The replaced DP_RECV block (later on referred to as the “DP_RECV monitor”) is meant to monitor data sent by the frequency converter drives to the 315-2 CPU via CP 342-5 Profibus communication modules.(Citation: Wired W32.Stuxnet Feb 2011)
S0603 | Stuxnet | software | uses | Program Download | technique | [Stuxnet](https://collaborate.mitre.org/attackics/index.php/Software/S0010) infects PLCs with different code depending on the characteristics of the target system. An infection sequence consists of code blocks and data blocks that will be downloaded to the PLC to alter its behavior.(Citation: Wired W32.Stuxnet Feb 2011)
S0603 | Stuxnet | software | uses | Program Upload | technique | [Stuxnet](https://collaborate.mitre.org/attackics/index.php/Software/S0010) replaces the DLL responsible for reading projects from a PLC to the step7 software. This allows Stuxnet the ability to upload a program from the PLC.(Citation: Wired W32.Stuxnet Feb 2011)
S0603 | Stuxnet | software | uses | Project File Infection | technique | [Stuxnet](https://collaborate.mitre.org/attackics/index.php/Software/S0010) copies itself into Step 7 projects in such a way that it automatically executes when the Step 7 project is loaded.(Citation: Wired W32.Stuxnet Feb 2011)
S0603 | Stuxnet | software | uses | Remote Services | technique | [Stuxnet](https://collaborate.mitre.org/attackics/index.php/Software/S0010) executes malicious SQL commands in the WinCC database server to propagate to remote systems. The malicious SQL commands include xp_cmdshell, sp_dumpdbilog, and sp_addextendedproc.(Citation: Wired W32.Stuxnet Feb 2011)
S0603 | Stuxnet | software | uses | Remote System Information Discovery | technique | [Stuxnet](https://collaborate.mitre.org/attackics/index.php/Software/S0010) enumerates and parses the System Data Blocks (SDB) using the s7blk_findfirst and s7blk_findnext API calls in s7otbxdx.dll. Stuxnet must find an SDB with the DWORD at offset 50h equal to 0100CB2Ch. This specifies that the system uses the Profibus communications processor module CP 342-5. In addition, specific values are searched for and counted: 7050h and 9500h. 7050h is assigned to part number KFC750V3 which appears to be a frequency converter drive (also known as variable frequency drive) manufactured by Fararo Paya in Teheran, Iran. 9500h is assigned to Vacon NX frequency converter drives manufactured by Vacon based in Finland.(Citation: Wired W32.Stuxnet Feb 2011)
S0603 | Stuxnet | software | uses | Remote System Information Discovery | technique | [Stuxnet](https://collaborate.mitre.org/attackics/index.php/Software/S0010) was specifically targeting CPUs 6ES7-315-2 (Series 300) with special system data block characteristics for sequence A or B and 6ES7-315-2 for sequence C. The PLC type can also be checked using the s7ag_read_szl API.(Citation: Wired W32.Stuxnet Feb 2011)
S0603 | Stuxnet | software | uses | Replication Through Removable Media | technique | [Stuxnet](https://collaborate.mitre.org/attackics/index.php/Software/S0010) was able to self-replicate by being spread through removable drives. A willing insider or unknown third party, such as a contractor, may have brought the removable media into the target environment.(Citation: Wired W32.Stuxnet Feb 2011) The earliest version of Stuxnet relied on physical installation, infecting target systems when an infected configuration file carried by a USB stick was opened.(Citation: Langner Nov 2013)
S0603 | Stuxnet | software | uses | Rootkit | technique | One of [Stuxnet](https://collaborate.mitre.org/attackics/index.php/Software/S0010) 's rootkits is contained entirely in the fake s7otbxdx.dll. In order to continue existing undetected on the PLC it needs to account for at least the following situations: read requests for its own malicious code blocks, read requests for infected blocks (OB1, OB35, DP_RECV), and write requests that could overwrite Stuxnet’s own code. Stuxnet contains code to monitor and intercept these types of requests. The rootkit modifies these requests so that Stuxnet’s PLC code is not discovered or damaged.(Citation: Langer Nov 2013)
S0603 | Stuxnet | software | uses | Rootkit | technique | When the peripheral output is written to, sequence C of[Stuxnet](https://collaborate.mitre.org/attackics/index.php/Software/S0010) intercepts the output and ensures it is not written to the process image output. The output is the instructions the PLC sends to a device to change its operating behavior. By intercepting the peripheral output, Stuxnet prevents an operator from noticing unauthorized commands sent to the peripheral(Citation: Wired W32.Stuxnet Feb 2011)
S0603 | Stuxnet | software | uses | Standard Application Layer Protocol | technique | [Stuxnet](https://collaborate.mitre.org/attackics/index.php/Software/S0010) uses a thread to monitor a data block DB890 of sequence A or B. This thread is constantly running and probing this block (every 5 minutes). On an infected PLC, if block DB890 is found and contains a special magic value (used by Stuxnet to identify his own block DB890), this block’s data can be read and written. This thread is likely used to optimize the way sequences A and B work, and modify their behavior when the Step7 editor is opened.(Citation: Wired W32.Stuxnet Feb 2011)
S0603 | Stuxnet | software | uses | Unauthorized Command Message | technique | [Stuxnet](https://collaborate.mitre.org/attackics/index.php/Software/S0010) sends two network bursts (done through the DP_SEND primitive). The data in the frames are instructions for the frequency converter drives. (Citation: Wired W32.Stuxnet Feb 2011)
| Triton | software | uses | Change Operating Mode | technique | [Triton](https://collaborate.mitre.org/attackics/index.php/Software/S0013) is able to modify code if the Triconex SIS Controller is configured with the physical keyswitch in ‘program mode’ during operation. If the controller is placed in Run mode (program changes not permitted), arbitrary changes in logic are not possible substantially reducing the likelihood of manipulation. Once the Triton implant is installed on the SIS it is able to conduct any operation regardless of any future position of the keyswitch.(Citation: FireEye TRITON Dec 2017)
| Triton | software | uses | Commonly Used Port | technique | [Triton](https://collaborate.mitre.org/attackics/index.php/Software/S0013) uses TriStation’s default UDP port, 1502, to communicate with devices.(Citation: MDudek-ICS TRISIS-TRITON-HATMAN)
| Triton | software | uses | Detect Operating Mode | technique | [Triton](https://collaborate.mitre.org/attackics/index.php/Software/S0013) contains a file named TS_cnames.py which contains default definitions for key state (TS_keystate). Key state is referenced in TsHi.py.(Citation: MDudek-ICS TRISIS-TRITON-HATMAN)
| Triton | software | uses | Execution through API | technique | [Triton](https://collaborate.mitre.org/attackics/index.php/Software/S0013) leverages a reconstructed TriStation protocol within its framework to trigger APIs related to program download, program allocation, and program changes.(Citation: Midnight Blue Labs TRITON Jan 2018)
| Triton | software | uses | Exploitation for Evasion | technique | [Triton](https://collaborate.mitre.org/attackics/index.php/Software/S0013) disables a firmware RAM/ROM consistency check, injects a payload (imain.bin) into the firmware memory region, and changes a jumptable entry to point to the added code(Citation: DHS CISA MAR-17-351-01 HatMan Feb 2019)(Citation: CISA Advisory (ICSA-18-107-02) Dec 2018)(Citation: Schneider Electric TRITON Jan 2018)In Schneider Electric Triconex Tricon MP model 3008 firmware versions 10.0-10.4, system calls read directly from memory addresses within the control program area without any verification. Manipulating this data could allow adversary data to be copied anywhere within memory.(Citation: MITRE CVE-2018-8872 May 2018)(Citation: CWE-119 Jan 2019)Triconex systems include continuous means of detection including checksums for firmware and program integrity, memory and memory reference integrity, and configuration.(Citation: NRC Triconex)
| Triton | software | uses | Exploitation for Privilege Escalation | technique | [Triton](https://collaborate.mitre.org/attackics/index.php/Software/S0013)leverages a previously-unknown vulnerability affecting Tricon MP3008 firmware versions 10.0–10.4 allows an insecurely-written system call to be exploited to achieve an arbitrary 2-byte write primitive, which is then used to gain supervisor privileges.(Citation: CISA MAR-17-352-01 February 2019)
| Triton | software | uses | Indicator Removal on Host | technique | [Triton](https://collaborate.mitre.org/attackics/index.php/Software/S0013) would reset the controller to the previous state over TriStation and if this failed it would write a dummy program to memory in what was likely an attempt at anti-forensics.(Citation: Midnight Blue Labs TRITON Jan 2018)
| Triton | software | uses | Loss of Safety | technique | [Triton](https://collaborate.mitre.org/attackics/index.php/Software/S0013) has the capability to reprogram the SIS logic to allow unsafe conditions to persist or reprogram the SIS to allow an unsafe state – while using the DCS to create an unsafe state or hazard.(Citation: FireEye TRITON Dec 2017)
| Triton | software | uses | Masquerading | technique | The [Triton](https://collaborate.mitre.org/attackics/index.php/Software/S0013), malware was configured to masquerade as trilog.exe, which is the Triconex software for analyzing SIS logs.(Citation: FireEye TRITON Dec 2017)
| Triton | software | uses | Modify Controller Tasking | technique | [Triton](https://collaborate.mitre.org/attackics/index.php/Software/S0013)'s 'argument-setting' and inject.bin shellcode are added to the program table on the Tricon so that they are executed by the firmware once each cycle.(Citation: CISA MAR-17-352-01 February 2019)(Citation: Midnight Blue Labs Triton January 2018)
| Triton | software | uses | Native API | technique | [Triton](https://collaborate.mitre.org/attackics/index.php/Software/S0013)'s imain.bin payload takes commands from the TsHi.ExplReadRam(Ex), TsHi.ExplWriteRam(Ex) and TsHi.ExplExec functions to perform operations on controller memory and registers using syscalls written in PowerPC shellcode.(Citation: Midnight Blue Labs Triton January 2018)
| Triton | software | uses | Program Download | technique | [Triton](https://collaborate.mitre.org/attackics/index.php/Software/S0013) leveraged the TriStation protocol to download programs onto Triconex Safety Instrumented System.(Citation: Midnight Blue Labs TRITON Jan 2018)
| Triton | software | uses | Remote System Discovery | technique | [Triton](https://collaborate.mitre.org/attackics/index.php/Software/S0013) uses a Python script that is capable of detecting Triconex controllers on the network by sending a specific UDP broadcast packet over port 1502.(Citation: DHS CISA MAR-17-351-01 HatMan Feb 2019)
| Triton | software | uses | Scripting | technique | In the version of [Triton](https://collaborate.mitre.org/attackics/index.php/Software/S0013) available at the time of publication, the component that programs the Triconex controllers is written entirely in Python. The modules that implement the communciation protocol and other supporting components are found in a separate file -- library.zip -- which the main script that employs this functionality is compiled into a standalone Windows executable -- trilog.exe -- that includes a Python environment.(Citation: DHS CISA MAR-17-351-01 HatMan Feb 2019)
| Triton | software | uses | Scripting | technique | A Python script seen in [Triton](https://collaborate.mitre.org/attackics/index.php/Software/S0013) communicates using four Python modules—TsBase, TsLow, TsHi, and TS_cnames—that collectively implement the TriStation network protocol ('TS', via UDP 1502); this is the protocol that the TriStation TS1131 software uses to communicate with Triconex safety PLCs.(Citation: DHS CISA MAR-17-351-01 HatMan Feb 2019)
| Triton | software | uses | Standard Application Layer Protocol | technique | [Triton](https://collaborate.mitre.org/attackics/index.php/Software/S0013) can communicate with the implant utilizing the TriStation 'get main processor diagnostic data' command and looks for a specifically crafted packet body from which it extracts a command value and its arguments.(Citation: Midnight Blue Labs TRITON Jan 2018)
| Triton | software | uses | System Firmware | technique | [Triton](https://collaborate.mitre.org/attackics/index.php/Software/S0013) is able to read, write and execute code in memory on the safety controller at an arbitrary address within the device’s firmware region. This allows the malware to make changes to the running firmware in memory and modify how the device operates.(Citation: DHS CISA MAR-17-351-01 HatMan Feb 2019)
| VPNFilter | software | uses | Network Sniffing | technique | The [VPNFilter](https://collaborate.mitre.org/attackics/index.php/Software/S0002) packet sniffer looks for basic authentication as well as monitors ICS traffic, and is specific to the TP-LINK R600-VPN. The malware uses a raw socket to look for connections to a pre-specified IP address, only looking at TCP packets that are 150 bytes or larger. Packets that are not on port 502, are scanned for BasicAuth, and that information is logged. This may have allowed credential harvesting from communications between devices accessing a modbus-enabled HMI.(Citation: Talos VPNFilter Jun 2018)(Citation: VPNFilter Deep Dive Mar 2019)
S0366 | WannaCry | software | uses | Exploitation of Remote Services | technique | [WannaCry](https://collaborate.mitre.org/attackics/index.php/Software/S0007) initially infected IT networks, but by means of an exploit (particularly the SMBv1-targeting MS17-010 vulnerability) spread to industrial networks.(Citation: Dragos Apr 2019)
S0366 | WannaCry | software | uses | External Remote Services | technique | [WannaCry](https://collaborate.mitre.org/attackics/index.php/Software/S0007) can utilize exposed SMB services to access industrial networks.(Citation: Dragos Apr 2019)
S0366 | WannaCry | software | uses | Lateral Tool Transfer | technique | [WannaCry](https://collaborate.mitre.org/attackics/index.php/Software/S0007) can move laterally through industrial networks by means of the SMB service.(Citation: Dragos Apr 2019)

## associated mitigations
source ID | source name | source type | mapping type | target name | target type | mapping description
| Access Management | mitigation | mitigates | Activate Firmware Update Mode | technique | All devices or systems changes, including all administrative functions, should require authentication. Consider using access management technologies to enforce authorization on all management interface access attempts, especially when the device does not inherently provide strong authentication and authorization functions.
| Access Management | mitigation | mitigates | Change Operating Mode | technique | Authenticate all access to field controllers before authorizing access to, or modification of, a device's state, logic, or programs. Centralized authentication techniques can help manage the large number of field controller accounts needed across the ICS.
| Access Management | mitigation | mitigates | Default Credentials | technique | Ensure embedded controls and network devices are protected through access management, as these devices often have unknown default accounts which could be used to gain unauthorized access.
| Access Management | mitigation | mitigates | Detect Operating Mode | technique | Authenticate all access to field controllers before authorizing access to, or modification of, a device's state, logic, or programs. Centralized authentication techniques can help manage the large number of field controller accounts needed across the ICS.
| Access Management | mitigation | mitigates | Device Restart/Shutdown | technique | All devices or systems changes, including all administrative functions, should require authentication. Consider using access management technologies to enforce authorization on all management interface access attempts, especially when the device does not inherently provide strong authentication and authorization functions.
| Access Management | mitigation | mitigates | Execution through API | technique | Access Management technologies can be used to enforce authorization policies and decisions, especially when existing field devices do not provided capabilities to support user identification and authentication.1 These technologies typically utilize an in-line network device or gateway system to prevent access to unauthenticated users, while also integrating with an authentication service to first verify user credentials.
| Access Management | mitigation | mitigates | Modify Alarm Settings | technique | All devices or systems changes, including all administrative functions, should require authentication. Consider using access management technologies to enforce authorization on all management interface access attempts, especially when the device does not inherently provide strong authentication and authorization functions.
| Access Management | mitigation | mitigates | Module Firmware | technique | All devices or systems changes, including all administrative functions, should require authentication. Consider using access management technologies to enforce authorization on all management interface access attempts, especially when the device does not inherently provide strong authentication and authorization functions.
| Access Management | mitigation | mitigates | Point & Tag Identification | technique | Authenticate all access to field controllers before authorizing access to, or modification of, a device's state, logic, or programs. Centralized authentication techniques can help manage the large number of field controller accounts needed across the ICS.
| Access Management | mitigation | mitigates | Program Download | technique | Authenticate all access to field controllers before authorizing access to, or modification of, a device's state, logic, or programs. Centralized authentication techniques can help manage the large number of field controller accounts needed across the ICS.
| Access Management | mitigation | mitigates | Program Upload | technique | Authenticate all access to field controllers before authorizing access to, or modification of, a device's state, logic, or programs. Centralized authentication techniques can help manage the large number of field controller accounts needed across the ICS.
| Access Management | mitigation | mitigates | Remote Services | technique | Access Management technologies can help enforce authentication on critical remote service, examples include, but are not limited to, device management services (e.g., telnet, SSH), data access servers (e.g., HTTP, Historians), and HMI sessions (e.g., RDP, VNC).
| Access Management | mitigation | mitigates | System Firmware | technique | All devices or systems changes, including all administrative functions, should require authentication. Consider using access management technologies to enforce authorization on all management interface access attempts, especially when the device does not inherently provide strong authentication and authorization functions.
| Access Management | mitigation | mitigates | Valid Accounts | technique | Authenticate all access to field controllers before authorizing access to, or modification of, a device's state, logic, or programs. Centralized authentication techniques can help manage the large number of field controller accounts needed across the ICS.
| Account Use Policies | mitigation | mitigates | External Remote Services | technique | Configure features related to account use like login attempt lockouts, specific login times, and password strength requirements as examples. Consider these features as they relate to assets which may impact safety and availability.
| Account Use Policies | mitigation | mitigates | Valid Accounts | technique | Configure features related to account use like login attempt lockouts, specific login times, and password strength requirements as examples. Consider these features as they relate to assets which may impact safety and availability.
| Active Directory Configuration | mitigation | mitigates | Valid Accounts | technique | Consider configuration and use of a network-wide authentication service such as Active Directory, LDAP, or RADIUS capabilities which can be found in ICS devices.
| Antivirus/Antimalware | mitigation | mitigates | Spearphishing Attachment | technique | Deploy anti-virus on all systems that support external email.
| Antivirus/Antimalware | mitigation | mitigates | Transient Cyber Asset | technique | Install anti-virus software on all workstation and transient assets that may have external access, such as to web, email, or remote file shares.
| Antivirus/Antimalware | mitigation | mitigates | User Execution | technique | Ensure anti-virus solution can detect malicious files that allow user execution (e.g., Microsoft Office Macros, program installers).
| Application Developer Guidance | mitigation | mitigates | Valid Accounts | technique | Ensure that applications and devices do not store sensitive data or credentials insecurely (e.g., plaintext credentials in code, published credentials in repositories, or credentials in public cloud storage).
| Application Isolation and Sandboxing | mitigation | mitigates | Drive-by Compromise | technique | Built-in browser sandboxes and application isolation may be used in conjunction to contain malware before malicious actions occur.
| Application Isolation and Sandboxing | mitigation | mitigates | Exploit Public-Facing Application | technique | Application isolation will limit the other processes and system features an exploited target can access. Examples of built in features are software restriction policies, AppLocker for Windows, and SELinux or AppArmor for Linux.
| Application Isolation and Sandboxing | mitigation | mitigates | Exploitation for Evasion | technique | Make it difficult for adversaries to advance their operation through exploitation of undiscovered or unpatched vulnerabilities by using sandboxing. Other types of virtualization and application microsegmentation may also mitigate the impact of some types of exploitation. Risks of additional exploits and weaknesses in these systems may still exist.
| Application Isolation and Sandboxing | mitigation | mitigates | Exploitation for Privilege Escalation | technique | Make it difficult for adversaries to advance their operation through exploitation of undiscovered or unpatched vulnerabilities by using sandboxing. Other types of virtualization and application microsegmentation may also mitigate the impact of some types of exploitation. Risks of additional exploits and weaknesses in these systems may still exist.
| Application Isolation and Sandboxing | mitigation | mitigates | Exploitation of Remote Services | technique | Make it difficult for adversaries to advance their operation through exploitation of undiscovered or unpatched vulnerabilities by using sandboxing. Other types of virtualization and application microsegmentation may also mitigate the impact of some types of exploitation. Risks of additional exploits and weaknesses in these systems may still exist.
| Application Isolation and Sandboxing | mitigation | mitigates | Scripting | technique | Consider the use of application isolation and sandboxing to restrict specific operating system interactions such as access through user accounts, services, system calls, registry, and network access. This may be even more useful in cases where the source of the executed script is unknown.
| Audit | mitigation | mitigates | Block Reporting Message | technique | Perform integrity checks of firmware before uploading it on a device. Utilize cryptographic hashes to verify the firmware has not been tampered with by comparing it a trusted hash of the firmware. This could be from a trusted data sources (e.g., vendor site) or through a third-party verification service.
| Audit | mitigation | mitigates | Data from Information Repositories | technique | Consider periodic review of accounts and privileges for critical and sensitive repositories.
| Audit | mitigation | mitigates | Hooking | technique | Perform audits or scans of systems, permissions, insecure software, insecure configurations, etc. to identify potential weaknesses. Perform periodic integrity checks of the device to validate the correctness of the firmware, software, programs, and configurations. Integrity checks, which typically include cryptographic hashes or digital signatures, should be compared to those obtained at known valid states, especially after events like device reboots, program downloads, or program restarts.
| Audit | mitigation | mitigates | Modify Controller Tasking | technique | Provide the ability to verify the integrity of control logic or programs loaded on a controller. While techniques like CRCs and checksums are commonly used, they are not cryptographically strong and can be vulnerable to collisions. Preferably cryptographic hash functions (e.g., SHA-2, SHA-3) should be used.
| Audit | mitigation | mitigates | Modify Parameter | technique | Provide the ability to verify the integrity of control logic or programs loaded on a controller. While techniques like CRCs and checksums are commonly used, they are not cryptographically strong and can be vulnerable to collisions. Preferably cryptographic hash functions (e.g., SHA-2, SHA-3) should be used.
| Audit | mitigation | mitigates | Modify Program | technique | Provide the ability to verify the integrity of control logic or programs loaded on a controller. While techniques like CRCs and checksums are commonly used, they are not cryptographically strong and can be vulnerable to collisions. Preferably cryptographic hash functions (e.g., SHA-2, SHA-3) should be used.
| Audit | mitigation | mitigates | Module Firmware | technique | Perform integrity checks of firmware before uploading it on a device. Utilize cryptographic hashes to verify the firmware has not been tampered with by comparing it a trusted hash of the firmware. This could be from a trusted data sources (e.g., vendor site) or through a third-party verification service.
| Audit | mitigation | mitigates | Program Download | technique | Provide the ability to verify the integrity of control logic or programs loaded on a controller. While techniques like CRCs and checksums are commonly used, they are not cryptographically strong and can be vulnerable to collisions. Preferably cryptographic hash functions (e.g., SHA-2, SHA-3) should be used.
| Audit | mitigation | mitigates | Project File Infection | technique | Review the integrity of project files to verify they have not been modified by adversary behavior. Verify a cryptographic hash for the file with a known trusted version, or look for other indicators of modification (e.g., timestamps).
| Audit | mitigation | mitigates | Rootkit | technique | Audit the integrity of PLC operating system functionality, such as the manipulation of standard function blocks (e.g., Organizational Blocks) that manage the execution of application logic programs.
| Audit | mitigation | mitigates | Supply Chain Compromise | technique | Perform audits or scans of systems, permissions, insecure software, insecure configurations, etc. to identify potential weaknesses. Perform periodic integrity checks of the device to validate the correctness of the firmware, software, programs, and configurations. Integrity checks, which typically include cryptographic hashes or digital signatures, should be compared to those obtained at known valid states, especially after events like device reboots, program downloads, or program restarts.
| Audit | mitigation | mitigates | System Firmware | technique | Perform integrity checks of firmware before uploading it on a device. Utilize cryptographic hashes to verify the firmware has not been tampered with by comparing it a trusted hash of the firmware. This could be from a trusted data sources (e.g., vendor site) or through a third-party verification service.
| Audit | mitigation | mitigates | Transient Cyber Asset | technique | Integrity checking of transient assets can include performing the validation of the booted operating system and programs using TPM-based technologies, such as Secure Boot and Trusted Boot.5 It can also include verifying filesystem changes, such as programs and configuration files stored on the system, executing processes, libraries, accounts, and open ports.
| Audit | mitigation | mitigates | Valid Accounts | technique | Routinely audit source code, application configuration files, open repositories, and public cloud storage for insecure use and storage of credentials.
| Authorization Enforcement | mitigation | mitigates | Activate Firmware Update Mode | technique | Restrict configurations changes and firmware updating abilities to only authorized individuals.
| Authorization Enforcement | mitigation | mitigates | Change Operating Mode | technique | All field controllers should restrict operating mode changes to only required authenticated users (e.g., engineers, field technicians), preferably through implementing a role-based access mechanism. Further, physical mechanisms (e.g., keys) can also be used to limit unauthorized operating mode changes.
| Authorization Enforcement | mitigation | mitigates | Detect Operating Mode | technique | All field controllers should restrict the modification of programs to only certain users (e.g., engineers, field technician), preferably through implementing a role-based access mechanism.
| Authorization Enforcement | mitigation | mitigates | Device Restart/Shutdown | technique | All field controllers should restrict the modification of programs to only certain users (e.g., engineers, field technician), preferably through implementing a role-based access mechanism.
| Authorization Enforcement | mitigation | mitigates | Execution through API | technique | All APIs used to perform execution, especially those hosted on embedded controllers (e.g., PLCs), should provide adequate authorization enforcement of user access. Minimize user's access to only required API calls.
| Authorization Enforcement | mitigation | mitigates | Modify Alarm Settings | technique | Only authorized personnel should be able to change settings for alarms.
| Authorization Enforcement | mitigation | mitigates | Modify Parameter | technique | All field controllers should restrict the modification of programs to only certain users (e.g., engineers, field technician), preferably through implementing a role-based access mechanism.
| Authorization Enforcement | mitigation | mitigates | Point & Tag Identification | technique | Automation protocols (e.g., OPC, DNP3) can restrict access to certain 'points'/requests based on a user's or device's privilege, this can prevent an unauthorized user from identifying certain point or tag identifiers. For example, DNP3-SA requires challenge-response authentication for certain DNP3 requests, similar techniques could be extended more broadly to other points or tags. Systems and devices should restrict access to any data with potential confidentiality concerns, including point and tag information.
| Authorization Enforcement | mitigation | mitigates | Program Download | technique | All field controllers should restrict the modification of programs to only certain users (e.g., engineers, field technician), preferably through implementing a role-based access mechanism.
| Authorization Enforcement | mitigation | mitigates | Program Upload | technique | All field controllers should restrict program uploads to only certain users (e.g., engineers, field technician), preferably through implementing a role-based access mechanism.
| Authorization Enforcement | mitigation | mitigates | Remote Services | technique | Provide privileges corresponding to the restriction of a GUI session to control system operations (examples include HMI read-only vs. read-write modes). Ensure local users, such as operators and engineers, are giving prioritization over remote sessions and have the authority to regain control over a remote session if needed. Prevent remote access sessions (e.g., RDP, VNC) from taking over local sessions, especially those used for ICS control, especially HMIs.
| Boot Integrity | mitigation | mitigates | Module Firmware | technique | Check the integrity of the existing BIOS or EFI to determine if it is vulnerable to modification. Use Trusted Platform Module technology. Move system's root of trust to hardware to prevent tampering with the SPI flash memory. Technologies such as Intel Boot Guard can assist with this.
| Boot Integrity | mitigation | mitigates | System Firmware | technique | Check the integrity of the existing BIOS or EFI to determine if it is vulnerable to modification. Use Trusted Platform Module technology. Move system's root of trust to hardware to prevent tampering with the SPI flash memory. Technologies such as Intel Boot Guard can assist with this.
| Code Signing | mitigation | mitigates | Block Reporting Message | technique | Devices should verify that firmware has been properly signed by the vendor before allowing installation.
| Code Signing | mitigation | mitigates | Masquerading | technique | Require signed binaries.
| Code Signing | mitigation | mitigates | Modify Controller Tasking | technique | Utilize code signatures to verify the integrity of the installed program on safety or control assets has not been changed.
| Code Signing | mitigation | mitigates | Modify Program | technique | Utilize code signatures to verify the integrity of the installed program on safety or control assets has not been changed.
| Code Signing | mitigation | mitigates | Module Firmware | technique | Devices should verify that firmware has been properly signed by the vendor before allowing installation.
| Code Signing | mitigation | mitigates | Program Download | technique | Utilize code signatures to verify the integrity of the installed program on safety or control assets has not been changed.
| Code Signing | mitigation | mitigates | Project File Infection | technique | Allow for code signing of any project files stored at rest to prevent unauthorized tampering. Ensure the signing keys are not easily accessible on the same system.
| Code Signing | mitigation | mitigates | Rootkit | technique | Digital signatures may be used to ensure application DLLs are authentic prior to execution.
| Code Signing | mitigation | mitigates | Supply Chain Compromise | technique | When available utilize hardware and software root-of-trust to verify the authenticity of a system. This may be achieved through cryptographic means, such as digital signatures or hashes, of critical software and firmware throughout the supply chain.
| Code Signing | mitigation | mitigates | System Firmware | technique | Devices should verify that firmware has been properly signed by the vendor before allowing installation.
| Code Signing | mitigation | mitigates | User Execution | technique | Prevent the use of unsigned executables, such as installers and scripts.
| Communication Authenticity | mitigation | mitigates | Activate Firmware Update Mode | technique | Protocols used for device management should authenticate all network messages to prevent unauthorized system changes.
| Communication Authenticity | mitigation | mitigates | Change Operating Mode | technique | Protocols used for device management should authenticate all network messages to prevent unauthorized system changes.
| Communication Authenticity | mitigation | mitigates | Detect Operating Mode | technique | Protocols used for control functions should provide authenticity through MAC functions or digital signatures. If not, utilize bump-in-the-wire devices or VPNs to enforce communication authenticity between devices that are not capable of supporting this (e.g., legacy controllers, RTUs).
| Communication Authenticity | mitigation | mitigates | Device Restart/Shutdown | technique | Protocols used for control functions should provide authenticity through MAC functions or digital signatures. If not, utilize bump-in-the-wire devices or VPNs to enforce communication authenticity between devices that are not capable of supporting this (e.g., legacy controllers, RTUs).
| Communication Authenticity | mitigation | mitigates | Man in the Middle | technique | Communication authenticity will ensure that any messages tampered with through MITM can be detected, but cannot prevent eavesdropping on these. In addition, providing communication authenticity around various discovery protocols, such as DNS, can be used to prevent various MITM procedures.
| Communication Authenticity | mitigation | mitigates | Manipulation of Control | technique | Protocols used for control functions should provide authenticity through MAC functions or digital signatures. If not, utilize bump-in-the-wire devices or VPNs to enforce communication authenticity between devices that are not capable of supporting this (e.g., legacy controllers, RTUs).
| Communication Authenticity | mitigation | mitigates | Manipulation of View | technique | Protocols used for control functions should provide authenticity through MAC functions or digital signatures. If not, utilize bump-in-the-wire devices or VPNs to enforce communication authenticity between devices that are not capable of supporting this (e.g., legacy controllers, RTUs).
| Communication Authenticity | mitigation | mitigates | Module Firmware | technique | Protocols used for device management should authenticate all network messages to prevent unauthorized system changes.
| Communication Authenticity | mitigation | mitigates | Point & Tag Identification | technique | Protocols used for control functions should provide authenticity through MAC functions or digital signatures. If not, utilize bump-in-the-wire devices or VPNs to enforce communication authenticity between devices that are not capable of supporting this (e.g., legacy controllers, RTUs).
| Communication Authenticity | mitigation | mitigates | Program Download | technique | Protocols used for device management should authenticate all network messages to prevent unauthorized system changes.
| Communication Authenticity | mitigation | mitigates | Program Upload | technique | Protocols used for device management should authenticate all network messages to prevent unauthorized system changes.
| Communication Authenticity | mitigation | mitigates | Rogue Master | technique | Protocols used for control functions should provide authenticity through MAC functions or digital signatures. If not, utilize bump-in-the-wire devices or VPNs to enforce communication authenticity between devices that are not capable of supporting this (e.g., legacy controllers, RTUs).
| Communication Authenticity | mitigation | mitigates | Spoof Reporting Message | technique | Protocols used for control functions should provide authenticity through MAC functions or digital signatures. If not, utilize bump-in-the-wire devices or VPNs to enforce communication authenticity between devices that are not capable of supporting this (e.g., legacy controllers, RTUs).
| Communication Authenticity | mitigation | mitigates | System Firmware | technique | Protocols used for device management should authenticate all network messages to prevent unauthorized system changes.
| Communication Authenticity | mitigation | mitigates | Unauthorized Command Message | technique | Protocols used for control functions should provide authenticity through MAC functions or digital signatures. If not, utilize bump-in-the-wire devices or VPNs to enforce communication authenticity between devices that are not capable of supporting this (e.g., legacy controllers, RTUs).
| Communication Authenticity | mitigation | mitigates | Wireless Compromise | technique | Do not inherently rely on the authenticity provided by the network/link layer (e.g., 802.11, LTE, 802.15.4), as link layer equipment may have long lifespans and protocol vulnerabilities may not be easily patched. Provide defense-in-depth by implementing authenticity within the associated application-layer protocol, or through a network-layer VPN. Furthermore, ensure communications schemes provide strong replay protection, employing techniques such as timestamps or cryptographic nonces.
M0953 | Data Backup | mitigation | mitigates | Data Destruction | technique | Utilize central storage servers for critical operations where possible (e.g., historians) and keep remote backups. For outstations, use local redundant storage for event recorders. Have backup control system platforms, preferably as hot-standbys to respond immediately to data destruction event.
M0953 | Data Backup | mitigation | mitigates | Denial of Control | technique | Take and store data backups from end user systems and critical servers. Ensure backup and storage systems are hardened and kept separate from the corporate network to prevent compromise. Maintain and exercise incident response plans, including the management of 'gold-copy' back-up images and configurations for key systems to enable quick recovery and response to adversarial activities that impact control, view, or availability.
M0953 | Data Backup | mitigation | mitigates | Denial of View | technique | Take and store data backups from end user systems and critical servers. Ensure backup and storage systems are hardened and kept separate from the corporate network to prevent compromise. Maintain and exercise incident response plans, including the management of 'gold-copy' back-up images and configurations for key systems to enable quick recovery and response to adversarial activities that impact control, view, or availability.
M0953 | Data Backup | mitigation | mitigates | Loss of Availability | technique | Take and store data backups from end user systems and critical servers. Ensure backup and storage systems are hardened and kept separate from the corporate network to prevent compromise. Maintain and exercise incident response plans, including the management of 'gold-copy' back-up images and configurations for key systems to enable quick recovery and response to adversarial activities that impact control, view, or availability.
M0953 | Data Backup | mitigation | mitigates | Loss of Control | technique | Take and store data backups from end user systems and critical servers. Ensure backup and storage systems are hardened and kept separate from the corporate network to prevent compromise. Maintain and exercise incident response plans, including the management of 'gold-copy' back-up images and configurations for key systems to enable quick recovery and response to adversarial activities that impact control, view, or availability.
M0953 | Data Backup | mitigation | mitigates | Loss of Productivity and Revenue | technique | Take and store data backups from end user systems and critical servers. Ensure backup and storage systems are hardened and kept separate from the corporate network to prevent compromise. Maintain and exercise incident response plans, including the management of 'gold-copy' back-up images and configurations for key systems to enable quick recovery and response to adversarial activities that impact control, view, or availability.
M0953 | Data Backup | mitigation | mitigates | Loss of View | technique | Take and store data backups from end user systems and critical servers. Ensure backup and storage systems are hardened and kept separate from the corporate network to prevent compromise. Maintain and exercise incident response plans, including the management of 'gold-copy' back-up images and configurations for key systems to enable quick recovery and response to adversarial activities that impact control, view, or availability.
M0953 | Data Backup | mitigation | mitigates | Manipulation of Control | technique | Take and store data backups from end user systems and critical servers. Ensure backup and storage systems are hardened and kept separate from the corporate network to prevent compromise. Maintain and exercise incident response plans, including the management of 'gold-copy' back-up images and configurations for key systems to enable quick recovery and response to adversarial activities that impact control, view, or availability.
M0953 | Data Backup | mitigation | mitigates | Manipulation of View | technique | Take and store data backups from end user systems and critical servers. Ensure backup and storage systems are hardened and kept separate from the corporate network to prevent compromise. Maintain and exercise incident response plans, including the management of 'gold-copy' back-up images and configurations for key systems to enable quick recovery and response to adversarial activities that impact control, view, or availability.
| Data Loss Prevention | mitigation | mitigates | Theft of Operational Information | technique | Apply DLP to protect the confidentiality of information related to operational processes, facility locations, device configurations, programs, or databases that may have information that can be used to infer organizational trade-secrets, recipes, and other intellectual property (IP).
| Disable or Remove Feature or Program | mitigation | mitigates | Command-Line Interface | technique | Consider removing or restricting features that are unnecessary to an asset's intended function within the control environment.
| Disable or Remove Feature or Program | mitigation | mitigates | Commonly Used Port | technique | Ensure that unnecessary ports and services are closed to prevent risk of discovery and potential exploitation.
| Disable or Remove Feature or Program | mitigation | mitigates | Device Restart/Shutdown | technique | Ensure remote commands that enable device shutdown are disabled if they are not necessary. Examples including DNP3's 0x0D function code or unnecessary device management functions.
| Disable or Remove Feature or Program | mitigation | mitigates | Exploitation of Remote Services | technique | Ensure that unnecessary ports and services are closed to prevent risk of discovery and potential exploitation.
| Disable or Remove Feature or Program | mitigation | mitigates | External Remote Services | technique | Consider removal of remote services which are not regularly in use, or only enabling them when required (e.g. vendor remote access). Ensure all external remote access point (e.g., jump boxes, VPN concentrator) are configured with least functionality, especially the removal of unnecessary services.
| Disable or Remove Feature or Program | mitigation | mitigates | Man in the Middle | technique | Disable unnecessary legacy network protocols that may be used for MiTM if applicable.
| Disable or Remove Feature or Program | mitigation | mitigates | Remote System Information Discovery | technique | Ensure that unnecessary ports and services are closed to prevent risk of discovery and potential exploitation.
| Disable or Remove Feature or Program | mitigation | mitigates | Replication Through Removable Media | technique | Consider the disabling of features such as AutoRun.
| Disable or Remove Feature or Program | mitigation | mitigates | Scripting | technique | Consider removal or disabling of programs and features which may be used to run malicious scripts (e.g., scripting language IDEs, PowerShell, visual studio).
| Encrypt Network Traffic | mitigation | mitigates | Module Firmware | technique | The encryption of firmware should be considered to prevent adversaries from identifying possible vulnerabilities within the firmware.
| Encrypt Network Traffic | mitigation | mitigates | Network Sniffing | technique | Ensure that wired and/or wireless traffic is encrypted when feasible. Use best practices for authentication protocols, such as Kerberos, and ensure web traffic that may contain credentials is protected by SSL/TLS.
| Encrypt Network Traffic | mitigation | mitigates | System Firmware | technique | The encryption of firmware should be considered to prevent adversaries from identifying possible vulnerabilities within the firmware.
| Encrypt Network Traffic | mitigation | mitigates | Wireless Compromise | technique | Utilize strong cryptographic techniques and protocols to prevent eavesdropping on network communications.
| Encrypt Network Traffic | mitigation | mitigates | Wireless Sniffing | technique | Utilize strong cryptographic techniques and protocols to prevent eavesdropping on network communications.
| Encrypt Sensitive Information | mitigation | mitigates | Data from Information Repositories | technique | Information which is sensitive to the operation and architecture of the process environment may be encrypted to ensure confidentiality and restrict access to only those who need to know.
| Encrypt Sensitive Information | mitigation | mitigates | Module Firmware | technique | The encryption of firmware should be considered to prevent adversaries from identifying possible vulnerabilities within the firmware.
| Encrypt Sensitive Information | mitigation | mitigates | Project File Infection | technique | When at rest, project files should be encrypted to prevent unauthorized changes.
| Encrypt Sensitive Information | mitigation | mitigates | System Firmware | technique | The encryption of firmware should be considered to prevent adversaries from identifying possible vulnerabilities within the firmware.
| Encrypt Sensitive Information | mitigation | mitigates | Theft of Operational Information | technique | Encrypt any operational data with strong confidentiality requirements, including organizational trade-secrets, recipes, and other intellectual property (IP).
| Encrypt Sensitive Information | mitigation | mitigates | Transient Cyber Asset | technique | Consider implementing full disk encryption, especially if engineering workstations are transient assets that are more likely to be lost, stolen, or tampered with.
| Execution Prevention | mitigation | mitigates | Command-Line Interface | technique | Execution prevention may block malicious software from accessing protected resources through the command line interface.
| Execution Prevention | mitigation | mitigates | Execution through API | technique | Minimize the exposure of API calls that allow the execution of code.
| Execution Prevention | mitigation | mitigates | Masquerading | technique | Use tools that restrict program execution via application control by attributes other than file name for common system and application utilities.
| Execution Prevention | mitigation | mitigates | Native API | technique | Minimize the exposure of API calls that allow the execution of code.
| Execution Prevention | mitigation | mitigates | Scripting | technique | Execution prevention may prevent malicious scripts from accessing protected resources.
| Execution Prevention | mitigation | mitigates | User Execution | technique | Application control may be able to prevent the running of executables masquerading as other files.
| Exploit Protection | mitigation | mitigates | Drive-by Compromise | technique | Utilize exploit protection to prevent activities which may be exploited through malicious web sites.
| Exploit Protection | mitigation | mitigates | Exploit Public-Facing Application | technique | Web Application Firewalls may be used to limit exposure of applications to prevent exploit traffic from reaching the application.
| Exploit Protection | mitigation | mitigates | Exploitation for Evasion | technique | Security applications that look for behavior used during exploitation such as Windows Defender Exploit Guard (WDEG) and the Enhanced Mitigation Experience Toolkit (EMET) can be used to mitigate some exploitation behavior. Control flow integrity checking is another way to potentially identify and stop a software exploit from occurring. Many of these protections depend on the architecture and target application binary for compatibility and may not work for all software or services targeted.
| Exploit Protection | mitigation | mitigates | Exploitation for Privilege Escalation | technique | Security applications that look for behavior used during exploitation such as Windows Defender Exploit Guard (WDEG) and the Enhanced Mitigation Experience Toolkit (EMET) can be used to mitigate some exploitation behavior. Control flow integrity checking is another way to potentially identify and stop a software exploit from occurring. Many of these protections depend on the architecture and target application binary for compatibility and may not work for all software or services targeted.
| Exploit Protection | mitigation | mitigates | Exploitation of Remote Services | technique | Security applications that look for behavior used during exploitation such as Windows Defender Exploit Guard (WDEG) and the Enhanced Mitigation Experience Toolkit (EMET) can be used to mitigate some exploitation behavior. Control flow integrity checking is another way to potentially identify and stop a software exploit from occurring. Many of these protections depend on the architecture and target application binary for compatibility and may not work for all software or services targeted.
| Filter Network Traffic | mitigation | mitigates | Activate Firmware Update Mode | technique | Filter for protocols and payloads associated with firmware activation or updating activity.
| Filter Network Traffic | mitigation | mitigates | Brute Force I/O | technique | Allow/denylists can be used to block access when excessive I/O connections are detected from a system or device during a specified time period.
| Filter Network Traffic | mitigation | mitigates | Connection Proxy | technique | Traffic to known anonymity networks and C2 infrastructure can be blocked through the use of network allow and block lists. It should be noted that this kind of blocking may be circumvented by other techniques like Domain Fronting.
| Filter Network Traffic | mitigation | mitigates | Detect Operating Mode | technique | Perform inline allowlisting of automation protocol commands to prevent devices from sending unauthorized command or reporting messages. Allow/denylist techniques need to be designed with sufficient accuracy to prevent the unintended blocking of valid messages.
| Filter Network Traffic | mitigation | mitigates | Device Restart/Shutdown | technique | Application denylists can be used to block automation protocol functions used to initiate device shutdowns or restarts, such as DNP3's 0x0D function code, or vulnerabilities that can be used to trigger device shutdowns (e.g., CVE-2014-9195, CVE-2015-5374).
| Filter Network Traffic | mitigation | mitigates | Man in the Middle | technique | Use network appliances and host-based security software to block network traffic that is not necessary within the environment, such as legacy protocols that may be leveraged for MiTM.
| Filter Network Traffic | mitigation | mitigates | Module Firmware | technique | Filter for protocols and payloads associated with firmware activation or updating activity.
| Filter Network Traffic | mitigation | mitigates | Point & Tag Identification | technique | Perform inline allowlisting of automation protocol commands to prevent devices from sending unauthorized command or reporting messages. Allow/denylist techniques need to be designed with sufficient accuracy to prevent the unintended blocking of valid messages.
| Filter Network Traffic | mitigation | mitigates | Program Download | technique | Filter for protocols and payloads associated with program download activity to prevent unauthorized device configurations.
| Filter Network Traffic | mitigation | mitigates | Program Upload | technique | Filter for protocols and payloads associated with program upload activity to prevent unauthorized access to device configurations.
| Filter Network Traffic | mitigation | mitigates | Remote Services | technique | Filter application-layer protocol messages for remote services to block any unauthorized activity.
| Filter Network Traffic | mitigation | mitigates | Rogue Master | technique | Perform inline allowlisting of automation protocol commands to prevent devices from sending unauthorized command or reporting messages. Allow/denylist techniques need to be designed with sufficient accuracy to prevent the unintended blocking of valid reporting messages.
| Filter Network Traffic | mitigation | mitigates | Spoof Reporting Message | technique | Perform inline allowlisting of automation protocol commands to prevent devices from sending unauthorized command or reporting messages. Allow/denylist techniques need to be designed with sufficient accuracy to prevent the unintended blocking of valid reporting messages.
| Filter Network Traffic | mitigation | mitigates | System Firmware | technique | Filter for protocols and payloads associated with firmware activation or updating activity.
| Filter Network Traffic | mitigation | mitigates | Unauthorized Command Message | technique | Perform inline allowlisting of automation protocol commands to prevent devices from sending unauthorized command or reporting messages. Allow/denylist techniques need to be designed with sufficient accuracy to prevent the unintended blocking of valid messages.
| Filter Network Traffic | mitigation | mitigates | Valid Accounts | technique | Consider using IP allowlisting along with user account management to ensure that data access is restricted not only to valid users but only from expected IP ranges to mitigate the use of stolen credentials to access data.
| Human User Authentication | mitigation | mitigates | Activate Firmware Update Mode | technique | Devices that allow remote management of firmware should require authentication before allowing any changes. The authentication mechanisms should also support Account Use Policies, Password Policies, and User Account Management
| Human User Authentication | mitigation | mitigates | Change Operating Mode | technique | All field controllers should require users to authenticate for all remote or local management sessions. The authentication mechanisms should also support Account Use Policies, Password Policies, and User Account Management.
| Human User Authentication | mitigation | mitigates | Commonly Used Port | technique | All field controllers should require users to authenticate for all remote or local management sessions. The authentication mechanisms should also support Account Use Policies, Password Policies, and User Account Management.
| Human User Authentication | mitigation | mitigates | Detect Operating Mode | technique | All field controllers should require users to authenticate for all remote or local management sessions. The authentication mechanisms should also support Account Use Policies, Password Policies, and User Account Management.
| Human User Authentication | mitigation | mitigates | Device Restart/Shutdown | technique | All field controllers should require users to authenticate for all remote or local management sessions. The authentication mechanisms should also support Account Use Policies, Password Policies, and User Account Management.
| Human User Authentication | mitigation | mitigates | Execution through API | technique | All APIs on remote systems or local processes should require the authentication of users before executing any code or system changes.
| Human User Authentication | mitigation | mitigates | Modify Alarm Settings | technique | All field controllers should require users to authenticate for all remote or local management sessions. The authentication mechanisms should also support Account Use Policies, Password Policies, and User Account Management.
| Human User Authentication | mitigation | mitigates | Module Firmware | technique | Devices that allow remote management of firmware should require authentication before allowing any changes. The authentication mechanisms should also support Account Use Policies, Password Policies, and User Account Management.
| Human User Authentication | mitigation | mitigates | Point & Tag Identification | technique | All field controllers should require users to authenticate for all remote or local management sessions. The authentication mechanisms should also support Account Use Policies, Password Policies, and User Account Management.
| Human User Authentication | mitigation | mitigates | Program Download | technique | All field controllers should require users to authenticate for all remote or local management sessions. The authentication mechanisms should also support Account Use Policies, Password Policies, and User Account Management.
| Human User Authentication | mitigation | mitigates | Program Upload | technique | All field controllers should require users to authenticate for all remote or local management sessions. The authentication mechanisms should also support Account Use Policies, Password Policies, and User Account Management.
| Human User Authentication | mitigation | mitigates | Remote Services | technique | All remote services should require strong authentication before providing user access.
| Human User Authentication | mitigation | mitigates | System Firmware | technique | Devices that allow remote management of firmware should require authentication before allowing any changes. The authentication mechanisms should also support Account Use Policies, Password Policies, and User Account Management.
| Limit Access to Resource Over Network | mitigation | mitigates | External Remote Services | technique | Limit access to remote services through centrally managed concentrators such as VPNs and other managed remote access systems.
| Limit Hardware Installation | mitigation | mitigates | Replication Through Removable Media | technique | Enforce system policies or physical restrictions to limit hardware such as USB devices on workstations.
| Mechanical Protection Layers | mitigation | mitigates | Damage to Property | technique | Protection devices should have minimal digital components to prevent exposure to related adversarial techniques. Examples include interlocks, rupture disk, release values, etc.
| Mechanical Protection Layers | mitigation | mitigates | Loss of Safety | technique | Protection devices should have minimal digital components to prevent exposure to related adversarial techniques. Examples include interlocks, rupture disk, release values, etc.
| Minimize Wireless Signal Propagation | mitigation | mitigates | Wireless Compromise | technique | Techniques can include (i) reducing transmission power on wireless signals, (ii) adjusting antenna gain to prevent extensions beyond organizational boundaries, and (iii) employing RF shielding techniques to block excessive signal propagation.
| Minimize Wireless Signal Propagation | mitigation | mitigates | Wireless Sniffing | technique | Reduce the range of RF communications to their intended operating range when possible. Propagation reduction methods may include (i) reducing transmission power on wireless signals, (ii) adjusting antenna gain to prevent extensions beyond organizational boundaries, and (iii) employing RF shielding techniques to block excessive signal propagation.
| Mitigation Limited or Not Effective | mitigation | mitigates | Graphical User Interface | technique | Once an adversary has access to a remote GUI they can abuse system features, such as required HMI functions.
| Mitigation Limited or Not Effective | mitigation | mitigates | I/O Image | technique | This technique may not be effectively mitigated against, consider controls for assets and processes that lead to the use of this technique.
| Mitigation Limited or Not Effective | mitigation | mitigates | Manipulate I/O Image | technique | This technique may not be effectively mitigated against, consider controls for assets and processes that lead to the use of this technique.
| Mitigation Limited or Not Effective | mitigation | mitigates | Monitor Process State | technique | This type of attack technique cannot be easily mitigated with preventive controls since it is based on the abuse of system features.
| Mitigation Limited or Not Effective | mitigation | mitigates | Network Connection Enumeration | technique | Network connection enumeration is likely obtained by using common system tools (e.g., netstat, ipconfig).
| Mitigation Limited or Not Effective | mitigation | mitigates | Screen Capture | technique | Preventing screen capture on a device may require disabling various system calls supported by the operating systems (e.g., Microsoft WindowsGraphicsCaputer APIs), however, these may be needed for other critical applications.
| Multi-factor Authentication | mitigation | mitigates | External Remote Services | technique | Use strong multi-factor authentication for remote service accounts to mitigate an adversary's ability to leverage stolen credentials. Be aware of multi-factor authentication interception techniques for some implementations.
| Multi-factor Authentication | mitigation | mitigates | Network Sniffing | technique | Use multi-factor authentication wherever possible.
| Multi-factor Authentication | mitigation | mitigates | Valid Accounts | technique | Integrating multi-factor authentication (MFA) as part of organizational policy can greatly reduce the risk of an adversary gaining access to valid credentials that may be used for additional tactics such as initial access, lateral movement, and collecting information. MFA can also be used to restrict access to cloud resources and APIs.
| Network Allowlists | mitigation | mitigates | Activate Firmware Update Mode | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations.
| Network Allowlists | mitigation | mitigates | Alarm Suppression | technique | Utilize network allowlists to restrict unnecessary connections to network devices (e.g., comm servers, serial to ethernet converters) and services, especially in cases when devices have limits on the number of simultaneous sessions they support.
| Network Allowlists | mitigation | mitigates | Automated Collection | technique | Utilize network allowlists to restrict unnecessary connections to network devices (e.g., comm servers, serial to ethernet converters) and services, especially in cases when devices have limits on the number of simultaneous sessions they support.
| Network Allowlists | mitigation | mitigates | Block Command Message | technique | Utilize network allowlists to restrict unnecessary connections to network devices (e.g., comm servers, serial to ethernet converters) and services, especially in cases when devices have limits on the number of simultaneous sessions they support.
| Network Allowlists | mitigation | mitigates | Block Reporting Message | technique | Utilize network allowlists to restrict unnecessary connections to network devices (e.g., comm servers, serial to ethernet converters) and services, especially in cases when devices have limits on the number of simultaneous sessions they support.
| Network Allowlists | mitigation | mitigates | Block Serial COM | technique | Implement network allowlists to minimize serial comm port access to only authorized hosts, such as comm servers and RTUs.
| Network Allowlists | mitigation | mitigates | Brute Force I/O | technique | Utilize network allowlists to restrict unnecessary connections to network devices (e.g., comm servers, serial to ethernet converters) and services, especially in cases when devices have limits on the number of simultaneous sessions they support.
| Network Allowlists | mitigation | mitigates | Change Operating Mode | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations.
| Network Allowlists | mitigation | mitigates | Connection Proxy | technique | Network allowlists can be implemented through either host-based files or system host files to specify what external connections (e.g., IP address, MAC address, port, protocol) can be made from a device. Allowlist techniques that operate at the application layer (e.g., DNP3, Modbus, HTTP) are addressed in the Filter Network Traffic mitigation.
| Network Allowlists | mitigation | mitigates | Damage to Property | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations.
| Network Allowlists | mitigation | mitigates | Detect Operating Mode | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations.
| Network Allowlists | mitigation | mitigates | Device Restart/Shutdown | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations.
| Network Allowlists | mitigation | mitigates | Modify Alarm Settings | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations.
| Network Allowlists | mitigation | mitigates | Module Firmware | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations.
| Network Allowlists | mitigation | mitigates | Point & Tag Identification | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations.
| Network Allowlists | mitigation | mitigates | Program Download | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations.
| Network Allowlists | mitigation | mitigates | Program Upload | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations.
| Network Allowlists | mitigation | mitigates | Remote Services | technique | Network allowlists can be implemented through either host-based files or system host files to specify what external connections (e.g., IP address, MAC address, port, protocol) can be made from a device.
| Network Allowlists | mitigation | mitigates | Rogue Master | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations.
| Network Allowlists | mitigation | mitigates | Spoof Reporting Message | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations.
| Network Allowlists | mitigation | mitigates | Standard Application Layer Protocol | technique | Network allowlists can be implemented through either host-based files or system host files to specify what external connections (e.g., IP address, MAC address, port, protocol) can be made from a device. Allowlist techniques that operate at the application layer (e.g., DNP3, Modbus, HTTP) are addressed in the Filter Network Traffic mitigation.
| Network Allowlists | mitigation | mitigates | System Firmware | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations.
| Network Allowlists | mitigation | mitigates | Unauthorized Command Message | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations.
| Network Intrusion Prevention | mitigation | mitigates | Commonly Used Port | technique | Network intrusion detection and prevention systems that use network signatures to identify traffic for specific adversary malware can be used to mitigate activity at the network level. Signatures are often for unique indicators within protocols and may be based on the specific protocol used by a particular adversary or tool and will likely be different across various malware families and versions. Adversaries will likely change tool C2 signatures over time or construct protocols in such a way as to avoid detection by common defensive tools.
| Network Intrusion Prevention | mitigation | mitigates | Connection Proxy | technique | Network intrusion detection and prevention systems that use network signatures to identify traffic for specific adversary malware can be used to mitigate activity at the network level. Signatures are often for unique indicators within protocols and may be based on the specific protocol used by a particular adversary or tool and will likely be different across various malware families and versions. Adversaries will likely change tool C2 signatures over time or construct protocols in such a way as to avoid detection by common defensive tools.
| Network Intrusion Prevention | mitigation | mitigates | Lateral Tool Transfer | technique | Network intrusion detection and prevention systems that use network signatures to identify traffic for specific adversary malware or unusual data transfer over known tools and protocols like FTP can be used to mitigate activity at the network level. Signatures are often for unique indicators within protocols and may be based on the specific obfuscation technique used by a particular adversary or tool and will likely be different across various malware families and versions. Adversaries will likely change tool C2 signatures over time or construct protocols in such a way as to avoid detection by common defensive tools.
| Network Intrusion Prevention | mitigation | mitigates | Man in the Middle | technique | Network intrusion detection and prevention systems that can identify traffic patterns indicative of MiTM activity can be used to mitigate activity at the network level.
| Network Intrusion Prevention | mitigation | mitigates | Remote System Information Discovery | technique | Use network intrusion detection/prevention systems to detect and prevent remote service scans.
| Network Intrusion Prevention | mitigation | mitigates | Spearphishing Attachment | technique | Network intrusion prevention systems and systems designed to scan and remove malicious email attachments can be used to block activity.
| Network Intrusion Prevention | mitigation | mitigates | Standard Application Layer Protocol | technique | Network intrusion detection and prevention systems that use network signatures to identify traffic for specific adversary malware can be used to mitigate activity at the network level.
| Network Intrusion Prevention | mitigation | mitigates | User Execution | technique | If a link is being visited by a user, network intrusion prevention systems and systems designed to scan and remove malicious downloads can be used to block activity.
| Network Segmentation | mitigation | mitigates | Activate Firmware Update Mode | technique | Segment operational network and systems to restrict access to critical system functions to predetermined management systems.
| Network Segmentation | mitigation | mitigates | Alarm Suppression | technique | Segment operational assets and their management devices based on their functional role within the process. Enabling more strict isolation to more critical control and operational information within the control environment.
| Network Segmentation | mitigation | mitigates | Automated Collection | technique | Prevent unauthorized systems from accessing control servers or field devices containing industrial information, especially services used for common automation protocols (e.g., DNP3, OPC).
| Network Segmentation | mitigation | mitigates | Block Serial COM | technique | Restrict unauthorized devices from accessing serial comm ports.
| Network Segmentation | mitigation | mitigates | Brute Force I/O | technique | Segment operational assets and their management devices based on their functional role within the process. Enabling more strict isolation to more critical control and operational information within the control environment.
| Network Segmentation | mitigation | mitigates | Change Operating Mode | technique | Segment operational network and systems to restrict access to critical system functions to predetermined management systems.
| Network Segmentation | mitigation | mitigates | Commonly Used Port | technique | Configure internal and external firewalls to block traffic using common ports that associate to network protocols that may be unnecessary for that particular network segment.
| Network Segmentation | mitigation | mitigates | Detect Operating Mode | technique | Segment operational network and systems to restrict access to critical system functions to predetermined management systems.
| Network Segmentation | mitigation | mitigates | Device Restart/Shutdown | technique | Segment operational network and systems to restrict access to critical system functions to predetermined management systems.
| Network Segmentation | mitigation | mitigates | Exploit Public-Facing Application | technique | Segment externally facing servers and services from the rest of the network with a DMZ or on separate hosting infrastructure.
| Network Segmentation | mitigation | mitigates | Exploitation of Remote Services | technique | Segment networks and systems appropriately to reduce access to critical system and services communications.
| Network Segmentation | mitigation | mitigates | External Remote Services | technique | Deny direct remote access to internal systems through the use of network proxies, gateways, and firewalls. Consider a jump server or host into the DMZ for greater access control. Leverage this DMZ or corporate resources for vendor access.
| Network Segmentation | mitigation | mitigates | Internet Accessible Device | technique | Deny direct remote access to internal systems through the use of network proxies, gateways, and firewalls. Steps should be taken to periodically inventory internet accessible devices to determine if it differs from the expected.
| Network Segmentation | mitigation | mitigates | Man in the Middle | technique | Network segmentation can be used to isolate infrastructure components that do not require broad network access. This may mitigate, or at least alleviate, the scope of MiTM activity.
| Network Segmentation | mitigation | mitigates | Modify Alarm Settings | technique | Segment operational network and systems to restrict access to critical system functions to predetermined management systems.
| Network Segmentation | mitigation | mitigates | Module Firmware | technique | Segment operational network and systems to restrict access to critical system functions to predetermined management systems.
| Network Segmentation | mitigation | mitigates | Network Sniffing | technique | Segment networks and systems appropriately to reduce access to critical system and services communications.
| Network Segmentation | mitigation | mitigates | Point & Tag Identification | technique | Segment operational assets and their management devices based on their functional role within the process. Enabling more strict isolation to more critical control and operational information within the control environment.
| Network Segmentation | mitigation | mitigates | Program Download | technique | Segment operational network and systems to restrict access to critical system functions to predetermined management systems.
| Network Segmentation | mitigation | mitigates | Program Upload | technique | Segment operational network and systems to restrict access to critical system functions to predetermined management systems.
| Network Segmentation | mitigation | mitigates | Remote Services | technique | Segment and control software movement between business and OT environments by way of one directional DMZs. Web access should be restricted from the OT environment. Engineering workstations, including transient cyber assets (TCAs) should have minimal connectivity to external networks, including Internet and email, further limit the extent to which these devices are dual-homed to multiple networks.
| Network Segmentation | mitigation | mitigates | Remote System Information Discovery | technique | Ensure proper network segmentation is followed to protect critical servers and devices.
| Network Segmentation | mitigation | mitigates | Rogue Master | technique | Segment operational assets and their management devices based on their functional role within the process. Enabling more strict isolation to more critical control and operational information within the control environment.
| Network Segmentation | mitigation | mitigates | Service Stop | technique | Segment operational network and systems to restrict access to critical system functions to predetermined management systems.
| Network Segmentation | mitigation | mitigates | Spoof Reporting Message | technique | Segment operational assets and their management devices based on their functional role within the process. Enabling more strict isolation to more critical control and operational information within the control environment.
| Network Segmentation | mitigation | mitigates | Standard Application Layer Protocol | technique | Ensure proper network segmentation between higher level corporate resources and the control process environment.
| Network Segmentation | mitigation | mitigates | System Firmware | technique | Segment operational network and systems to restrict access to critical system functions to predetermined management systems.
| Network Segmentation | mitigation | mitigates | Transient Cyber Asset | technique | Segment and control software movement between business and OT environments by way of one directional DMZs. Web access should be restricted from the OT environment. Engineering workstations, including transient cyber assets (TCAs) should have minimal connectivity to external networks, including Internet and email, further limit the extent to which these devices are dual-homed to multiple networks.
| Network Segmentation | mitigation | mitigates | Unauthorized Command Message | technique | Segment operational assets and their management devices based on their functional role within the process. Enabling more strict isolation to more critical control and operational information within the control environment.
| Operating System Configuration | mitigation | mitigates | Replication Through Removable Media | technique | Harden the system through operating system controls to prevent the known or unknown use of malicious removable media.
| Operational Information Confidentiality | mitigation | mitigates | Theft of Operational Information | technique | Example mitigations could include minimizing its distribution/storage or obfuscating the information (e.g., facility coverterms, codenames). In many cases this information may be necessary to support critical engineering, maintenance, or operational functions, therefore, it may not be feasible to implement.
| Out-of-Band Communications Channel | mitigation | mitigates | Alarm Suppression | technique | Provide an alternative method for alarms to be reported in the event of a communication failure.
| Out-of-Band Communications Channel | mitigation | mitigates | Block Command Message | technique | Provide an alternative method for sending critical commands message to outstations, this could include using radio/cell communication to send messages to a field technician that physically performs the control function.
| Out-of-Band Communications Channel | mitigation | mitigates | Block Reporting Message | technique | Provide an alternative method for sending critical report messages to operators, this could include using radio/cell communication to obtain messages from field technicians that can locally obtain telemetry and status data.
| Out-of-Band Communications Channel | mitigation | mitigates | Block Serial COM | technique | Ensure devices have an alternative method for communicating in the event that a valid COM port is unavailable.
| Out-of-Band Communications Channel | mitigation | mitigates | Denial of Control | technique | Provide operators with redundant, out-of-band communication to support monitoring and control of the operational processes, especially when recovering from a network outage. Out-of-band communication should utilize diverse systems and technologies to minimize common failure modes and vulnerabilities within the communications infrastructure. For example, wireless networks (e.g., 3G, 4G) can be used to provide diverse and redundant delivery of data.
| Out-of-Band Communications Channel | mitigation | mitigates | Denial of View | technique | Provide operators with redundant, out-of-band communication to support monitoring and control of the operational processes, especially when recovering from a network outage. Out-of-band communication should utilize diverse systems and technologies to minimize common failure modes and vulnerabilities within the communications infrastructure. For example, wireless networks (e.g., 3G, 4G) can be used to provide diverse and redundant delivery of data.
| Out-of-Band Communications Channel | mitigation | mitigates | Loss of Availability | technique | Provide operators with redundant, out-of-band communication to support monitoring and control of the operational processes, especially when recovering from a network outage. Out-of-band communication should utilize diverse systems and technologies to minimize common failure modes and vulnerabilities within the communications infrastructure. For example, wireless networks (e.g., 3G, 4G) can be used to provide diverse and redundant delivery of data.
| Out-of-Band Communications Channel | mitigation | mitigates | Loss of Control | technique | Provide operators with redundant, out-of-band communication to support monitoring and control of the operational processes, especially when recovering from a network outage. Out-of-band communication should utilize diverse systems and technologies to minimize common failure modes and vulnerabilities within the communications infrastructure. For example, wireless networks (e.g., 3G, 4G) can be used to provide diverse and redundant delivery of data.
| Out-of-Band Communications Channel | mitigation | mitigates | Loss of View | technique | Provide operators with redundant, out-of-band communication to support monitoring and control of the operational processes, especially when recovering from a network outage. Out-of-band communication should utilize diverse systems and technologies to minimize common failure modes and vulnerabilities within the communications infrastructure. For example, wireless networks (e.g., 3G, 4G) can be used to provide diverse and redundant delivery of data.
| Out-of-Band Communications Channel | mitigation | mitigates | Man in the Middle | technique | Utilize out-of-band communication to validate the integrity of data from the primary channel.
| Out-of-Band Communications Channel | mitigation | mitigates | Manipulation of Control | technique | Utilize out-of-band communication to validate the integrity of data from the primary channel.
| Out-of-Band Communications Channel | mitigation | mitigates | Manipulation of View | technique | Utilize out-of-band communication to validate the integrity of data from the primary channel.
| Password Policies | mitigation | mitigates | Default Credentials | technique | Review vendor documents and security alerts for potentially unknown or overlooked default credentials within existing devices
| Password Policies | mitigation | mitigates | External Remote Services | technique | Set and enforce secure password policies for accounts.
| Password Policies | mitigation | mitigates | Remote Services | technique | Enforce strong password requirements to prevent password brute force methods for lateral movement.
| Password Policies | mitigation | mitigates | Valid Accounts | technique | Applications and appliances that utilize default username and password should be changed immediately after the installation, and before deployment to a production environment.
| Privileged Account Management | mitigation | mitigates | Data Destruction | technique | Minimize permissions and access for service accounts to limit the information that may be impacted by malicious users or software.
| Privileged Account Management | mitigation | mitigates | Data from Information Repositories | technique | Minimize permissions and access for service accounts to limit the information that may be exposed or collected by malicious users or software.
| Privileged Account Management | mitigation | mitigates | Exploit Public-Facing Application | technique | Use least privilege for service accounts.
| Privileged Account Management | mitigation | mitigates | Exploitation of Remote Services | technique | Minimize permissions and access for service accounts to limit impact of exploitation.
| Privileged Account Management | mitigation | mitigates | Network Sniffing | technique | Restrict root or administrator access on user accounts to limit the ability to capture promiscuous traffic on a network through common packet capture tools.
| Privileged Account Management | mitigation | mitigates | Valid Accounts | technique | Audit domain and local accounts and their permission levels routinely to look for situations that could allow an adversary to gain system wide access with stolen privileged account credentials. These audits should also identify if default accounts have been enabled, or if new local accounts are created that have not be authorized. Follow best practices for design and administration of an enterprise network to limit privileged account use across administrative tiers.
| Redundancy of Service | mitigation | mitigates | Denial of Control | technique | Hot-standbys in diverse locations can ensure continued operations if the primarily system are compromised or unavailable. At the network layer, protocols such as the Parallel Redundancy Protocol can be used to simultaneously use redundant and diverse communication over a local network.
| Redundancy of Service | mitigation | mitigates | Denial of View | technique | Hot-standbys in diverse locations can ensure continued operations if the primarily system are compromised or unavailable. At the network layer, protocols such as the Parallel Redundancy Protocol can be used to simultaneously use redundant and diverse communication over a local network.
| Redundancy of Service | mitigation | mitigates | Loss of Availability | technique | Hot-standbys in diverse locations can ensure continued operations if the primarily system are compromised or unavailable. At the network layer, protocols such as the Parallel Redundancy Protocol can be used to simultaneously use redundant and diverse communication over a local network.
| Redundancy of Service | mitigation | mitigates | Loss of Control | technique | Hot-standbys in diverse locations can ensure continued operations if the primarily system are compromised or unavailable. At the network layer, protocols such as the Parallel Redundancy Protocol can be used to simultaneously use redundant and diverse communication over a local network.
| Redundancy of Service | mitigation | mitigates | Loss of View | technique | Hot-standbys in diverse locations can ensure continued operations if the primarily system are compromised or unavailable. At the network layer, protocols such as the Parallel Redundancy Protocol can be used to simultaneously use redundant and diverse communication over a local network.
| Restrict File and Directory Permissions | mitigation | mitigates | Data Destruction | technique | Protect files stored locally with proper permissions to limit opportunities for adversaries to impact data storage.
| Restrict File and Directory Permissions | mitigation | mitigates | Data from Information Repositories | technique | Protect files stored locally with proper permissions to limit opportunities for adversaries to interact and collect information from databases.
| Restrict File and Directory Permissions | mitigation | mitigates | Indicator Removal on Host | technique | Protect files stored locally with proper permissions to limit opportunities for adversaries to remove indicators of their activity on the system.
| Restrict File and Directory Permissions | mitigation | mitigates | Masquerading | technique | Use file system access controls to protect system and application folders.
| Restrict File and Directory Permissions | mitigation | mitigates | Project File Infection | technique | Ensure permissions restrict project file access to only engineer and technician user groups and accounts.
| Restrict File and Directory Permissions | mitigation | mitigates | Service Stop | technique | Ensure proper process and file permissions are in place to inhibit adversaries from disabling or interfering with critical services.
| Restrict File and Directory Permissions | mitigation | mitigates | Theft of Operational Information | technique | Protect files stored locally with proper permissions to limit opportunities for adversaries to interact and collect information from databases.
| Restrict Library Loading | mitigation | mitigates | Hooking | technique | Restrict the use of untrusted or unknown libraries, such as remote or unknown DLLs.
| Restrict Registry Permissions | mitigation | mitigates | Service Stop | technique | Ensure proper registry permissions are in place to inhibit adversaries from disabling or interfering with critical services.
| Restrict Web-Based Content | mitigation | mitigates | Drive-by Compromise | technique | Restrict browsers to limit the capabilities of malicious ads and Javascript.
| Restrict Web-Based Content | mitigation | mitigates | Spearphishing Attachment | technique | Consider restricting access to email within critical process environments. Additionally, downloads and attachments may be disabled if email is still necessary.
| Restrict Web-Based Content | mitigation | mitigates | User Execution | technique | If a link is being visited by a user, block unknown or unused files in transit by default that should not be downloaded or by policy from suspicious sites as a best practice to prevent some vectors, such as .scr, .exe, .pif, .cpl, etc. Some download scanning devices can open and analyze compressed and encrypted formats, such as zip and rar that may be used to conceal malicious files.
| SSL/TLS Inspection | mitigation | mitigates | Connection Proxy | technique | If it is possible to inspect HTTPS traffic, the captures can be analyzed for connections that appear to be domain fronting.
| Safety Instrumented Systems | mitigation | mitigates | Damage to Property | technique | Ensure that all SIS are segmented from operational networks to prevent them from being targeted by additional adversarial behavior.
| Safety Instrumented Systems | mitigation | mitigates | Loss of Safety | technique | Ensure that all SIS are segmented from operational networks to prevent them from being targeted by additional adversarial behavior.
| Software Process and Device Authentication | mitigation | mitigates | Activate Firmware Update Mode | technique | Authenticate connections from software and devices to prevent unauthorized systems from accessing protected management functions.
| Software Process and Device Authentication | mitigation | mitigates | Brute Force I/O | technique | Devices should authenticate all messages between master and outstation assets.
| Software Process and Device Authentication | mitigation | mitigates | Change Operating Mode | technique | Authenticate connections from software and devices to prevent unauthorized systems from accessing protected management functions.
| Software Process and Device Authentication | mitigation | mitigates | Detect Operating Mode | technique | Authenticate connections from software and devices to prevent unauthorized systems from accessing protected management functions.
| Software Process and Device Authentication | mitigation | mitigates | Device Restart/Shutdown | technique | Authenticate connections from software and devices to prevent unauthorized systems from accessing protected management functions.
| Software Process and Device Authentication | mitigation | mitigates | Man in the Middle | technique | To protect against MITM, authentication mechanisms should not send credentials across the network in plaintext and should also implement mechanisms to prevent replay attacks (such as nonces or timestamps). Challenge-response based authentication techniques that do not directly send credentials over the network provide better protection from MITM.
| Software Process and Device Authentication | mitigation | mitigates | Modify Alarm Settings | technique | Authenticate connections from software and devices to prevent unauthorized systems from accessing protected management functions.
| Software Process and Device Authentication | mitigation | mitigates | Module Firmware | technique | Authenticate connections from software and devices to prevent unauthorized systems from accessing protected management functions.
| Software Process and Device Authentication | mitigation | mitigates | Point & Tag Identification | technique | Devices should authenticate all messages between master and outstation assets.
| Software Process and Device Authentication | mitigation | mitigates | Program Download | technique | Authenticate connections from software and devices to prevent unauthorized systems from accessing protected management functions.
| Software Process and Device Authentication | mitigation | mitigates | Program Upload | technique | Authenticate connections from software and devices to prevent unauthorized systems from accessing protected management functions.
| Software Process and Device Authentication | mitigation | mitigates | Remote Services | technique | All communication sessions to remote services should be authenticated to prevent unauthorized access.
| Software Process and Device Authentication | mitigation | mitigates | Rogue Master | technique | Devices should authenticate all messages between master and outstation assets.
| Software Process and Device Authentication | mitigation | mitigates | Spoof Reporting Message | technique | Devices should authenticate all messages between master and outstation assets.
| Software Process and Device Authentication | mitigation | mitigates | System Firmware | technique | Authenticate connections from software and devices to prevent unauthorized systems from accessing protected management functions.
| Software Process and Device Authentication | mitigation | mitigates | Unauthorized Command Message | technique | Devices should authenticate all messages between master and outstation assets.
| Software Process and Device Authentication | mitigation | mitigates | Wireless Compromise | technique | Ensure wireless networks require the authentication of all devices, and that all wireless devices also authenticate network infrastructure devices (i.e., mutual authentication). For defense-in-depth purposes, utilize VPNs or ensure that application-layer protocols also authenticate the system or device. Use protocols that provide strong authentication (e.g., IEEE 802.1X), and enforce basic protections, such as MAC filtering, when stronger cryptographic techniques are not available.
| Static Network Configuration | mitigation | mitigates | Alarm Suppression | technique | Unauthorized connections can be prevented by statically defining the hosts and ports used for automation protocol connections.
| Static Network Configuration | mitigation | mitigates | Block Command Message | technique | Unauthorized connections can be prevented by statically defining the hosts and ports used for automation protocol connections.
| Static Network Configuration | mitigation | mitigates | Block Reporting Message | technique | Unauthorized connections can be prevented by statically defining the hosts and ports used for automation protocol connections.
| Static Network Configuration | mitigation | mitigates | Man in the Middle | technique | Statically defined ARP entries can prevent manipulation and sniffing of switched network traffic, as some MitM techniques depend on sending spoofed ARP messages to manipulate network host's dynamic ARP tables.
| Static Network Configuration | mitigation | mitigates | Network Sniffing | technique | Statically defined ARP entries can prevent manipulation and sniffing of switched network traffic, as some MitM techniques depend on sending spoofed ARP messages to manipulate network host's dynamic ARP tables.
| Static Network Configuration | mitigation | mitigates | Remote System Discovery | technique | Statically defined ARP entries can prevent manipulation and sniffing of switched network traffic, as some MitM techniques depend on sending spoofed ARP messages to manipulate network host's dynamic ARP tables.
| Static Network Configuration | mitigation | mitigates | Remote System Information Discovery | technique | ICS environments typically have more statically defined devices, therefore minimize the use of both IT discovery protocols (e.g., DHCP, LLDP) and discovery functions in automation protocols. Examples of automation protocols with discovery capabilities include OPC UA Device Discovery, BACnet, and Ethernet/IP.
| Supply Chain Management | mitigation | mitigates | Supply Chain Compromise | technique | A supply chain management program should include methods the assess the trustworthiness and technical maturity of a supplier, along with technical methods (e.g., code-signing, bill of materials) needed to validate the integrity of newly obtained devices and components. Develop procurement language that emphasizes the expectations for suppliers regarding the artifacts, audit records, and technical capabilities needed to validate the integrity of the device’s supply chain.
| Threat Intelligence Program | mitigation | mitigates | Exploitation for Evasion | technique | Develop a robust cyber threat intelligence capability to determine what types and levels of threat may use software exploits and 0-days against a particular organization.
| Threat Intelligence Program | mitigation | mitigates | Exploitation for Privilege Escalation | technique | Develop a robust cyber threat intelligence capability to determine what types and levels of threat may use software exploits and 0-days against a particular organization.
| Threat Intelligence Program | mitigation | mitigates | Exploitation of Remote Services | technique | Develop a robust cyber threat intelligence capability to determine what types and levels of threat may use software exploits and 0-days against a particular organization.
| Update Software | mitigation | mitigates | Drive-by Compromise | technique | Ensure all browsers and plugins are kept updated to help prevent the exploit phase of this technique. Use modern browsers with security features enabled.
| Update Software | mitigation | mitigates | Exploit Public-Facing Application | technique | Regularly scan externally facing systems for vulnerabilities and establish procedures to rapidly patch systems when critical vulnerabilities are discovered through scanning and public disclosure.
| Update Software | mitigation | mitigates | Exploitation for Evasion | technique | Update software regularly by employing patch management for internal enterprise endpoints and servers.
| Update Software | mitigation | mitigates | Exploitation for Privilege Escalation | technique | Update software regularly by employing patch management for internal enterprise endpoints and servers.
| Update Software | mitigation | mitigates | Exploitation of Remote Services | technique | Update software regularly by employing patch management for internal enterprise endpoints and servers.
| Update Software | mitigation | mitigates | Supply Chain Compromise | technique | A patch management process should be implemented to check unused dependencies, unmaintained and/or previously vulnerable dependencies, unnecessary features, components, files, and documentation.
| Update Software | mitigation | mitigates | System Firmware | technique | Patch the BIOS and EFI as necessary.
| Update Software | mitigation | mitigates | Transient Cyber Asset | technique | Update software on control network assets when possible. If feasible, use modern operating systems and software to reduce exposure to known vulnerabilities.
| User Account Management | mitigation | mitigates | Data from Information Repositories | technique | Ensure users and user groups have appropriate permissions for their roles through Identity and Access Management (IAM) controls to prevent misuse. Implement user accounts for each individual that may access the repositories for role enforcement and non-repudiation of actions.
| User Account Management | mitigation | mitigates | External Remote Services | technique | Consider utilizing jump boxes for external remote access. Additionally, dynamic account management may be used to easily remove accounts when not in use.
| User Account Management | mitigation | mitigates | Modify Alarm Settings | technique | Limit privileges of user accounts and groups so that only designated administrators or engineers can interact with alarm management and alarm configuration thresholds.
| User Account Management | mitigation | mitigates | Remote Services | technique | Limit the accounts that may use remote services. Limit the permissions for accounts that are at higher risk of compromise; for example, configure SSH so users can only run specific programs.
| User Account Management | mitigation | mitigates | Service Stop | technique | Limit privileges of user accounts and groups so that only authorized administrators can change service states and configurations.
| User Account Management | mitigation | mitigates | Valid Accounts | technique | Ensure users and user groups have appropriate permissions for their roles through Identity and Access Management (IAM) controls. Implement strict IAM controls to prevent access to systems except for the applications, users, and services that require access. Implement user accounts for each individual for enforcement and non-repudiation of actions.
| User Training | mitigation | mitigates | Data from Information Repositories | technique | Develop and publish policies that define acceptable information to be stored in repositories.
| User Training | mitigation | mitigates | Spearphishing Attachment | technique | Users can be trained to identify social engineering techniques and spearphishing emails.
| User Training | mitigation | mitigates | User Execution | technique | Use user training as a way to bring awareness to common phishing and spearphishing techniques and how to raise suspicion for potentially malicious events.
| Vulnerability Scanning | mitigation | mitigates | Exploit Public-Facing Application | technique | Regularly scan externally facing systems for vulnerabilities and establish procedures to rapidly patch systems when critical vulnerabilities are discovered through scanning and public disclosure.
| Vulnerability Scanning | mitigation | mitigates | Exploitation of Remote Services | technique | Regularly scan the internal network for available services to identify new and potentially vulnerable services.
| Vulnerability Scanning | mitigation | mitigates | Supply Chain Compromise | technique | Implement continuous monitoring of vulnerability sources. Also, use automatic and manual code review tools.
| Watchdog Timers | mitigation | mitigates | Denial of Service | technique | System and process restarts should be performed when a timeout condition occurs.

## citations
reference | citation | url
BankInfoSecurity Lyceum Aug 2019 | Jeffery Burt. (2019, August 30). Lyceum APT Group a Fresh Threat to Oil and Gas Companies. Retrieved January 3, 2020. | https://www.bankinfosecurity.com/lyceum-apt-group-new-threat-to-oil-gas-companies-a-13003
BlackHat Mar 2016 | Spenneberg, Ralf, Maik Brüggemann, and Hendrik Schwartke. (2016, March 31). Plc-blaster: A worm living solely in the plc.. Retrieved September 19, 2017. | https://www.blackhat.com/docs/asia-16/materials/asia-16-Spenneberg-PLC-Blaster-A-Worm-Living-Solely-In-The-PLC-wp.pdf
Bloomberg Dec 2019 | David Voreacos, Katherine Chinglinsky, Riley Griffin. (2019, December 03). Merck Cyberattack’s $1.3 Billion Question: Was It an Act of War?. Retrieved December 6, 2019. | https://www.bloomberg.com/news/features/2019-12-03/merck-cyberattack-s-1-3-billion-question-was-it-an-act-of-war
Booz Allen Hamilton | Booz Allen Hamilton. (n.d.). When The Lights Went Out. Retrieved October 22, 2019. | https://www.boozallen.com/content/dam/boozallen/documents/2016/09/ukraine-report-when-the-lights-went-out.pdf
CISA MAR-17-352-01 February 2019 | DHS CISA. (2019, February 27). MAR-17-352-01 HatMan—Safety System Targeted Malware (Update B). Retrieved March 8, 2019. | https://ics-cert.us-cert.gov/sites/default/files/documents/MAR-17-352-01%20HatMan%20-%20Safety%20System%20Targeted%20Malware%20%28Update%20B%29.pdf
CISA TA18-074A March 2018 | Cybersecurity & Infrastructure Security Agency. (2018, March 15). Alert (TA18-074A) Russian Government Cyber Activity Targeting Energy and Other Critical Infrastructure Sectors. Retrieved October 11, 2019. | https://us-cert.cisa.gov/ncas/alerts/TA18-074A
CWE-119 Jan 2019 | Common Weakness Enumeration. (2019, January 03). CWE-119: Improper Restriction of Operations within the Bounds of a Memory Buffer. Retrieved March 8, 2019. | https://cwe.mitre.org/data/definitions/119.html
CyberScoop Xenotime May 2018 | Chris Bing. (2018, May 24). Trisis masterminds have expanded operations to target U.S. industrial firms. Retrieved January 3, 2020. | https://www.cyberscoop.com/xenotime-ics-cyber-attacks-trisis-dragos/
CyberViser May 21 | REduard Kovacs. (2018, May 21). Group linked to Shamoon attacks targeting ICS networks in Middle East and UK. Retrieved January 3, 2020. | https://www.cyberviser.com/2018/05/group-linked-to-shamoon-attacks-targeting-ics-networks-in-middle-east-and-uk/
Cybereason Sodinokibi August 2019 | Tom Fakterman. (2019, August 05). Sodinokibi: The Crown Prince of Ransomware. Retrieved April 12, 2021. | https://www.cybereason.com/blog/the-sodinokibi-ransomware-attack
DHS CISA MAR-17-351-01 HatMan Feb 2019 | DHS CISA. (2019, February 27). MAR-17-352-01 HatMan—Safety System Targeted Malware (Update B). Retrieved March 8, 2019. | https://ics-cert.us-cert.gov/sites/default/files/documents/MAR-17-352-01%20HatMan%20-%20Safety%20System%20Targeted%20Malware%20%28Update%20B%29.pdf
DOJ Sandworm Team October 2020 | UNITED STATES DISTRICT COURT WESTERN DISTRICT OF PENNSYLVANIA. (2020, October 15). Indictment: Conspiracy to Commit an Offense Against the United States. Retrieved April 7, 2021. | https://www.justice.gov/opa/press-release/file/1328521/download
DarkReading | Kelly Jackson Higgins. (n.d.). How a Manufacturing Firm Recovered from a Devastating Ransomware Attack. Retrieved November 3, 2019. | https://www.darkreading.com/attacks-breaches/how-a-manufacturing-firm-recovered-from-a-devastating-ransomware-attack/d/d-id/1334760
Darktrace Sodinokibi Feb 2020 | Max Heinemeyer. (2020, February 21). Post-mortem of a targeted Sodinokibi ransomware attack. Retrieved April 12, 2021. | https://www.darktrace.com/en/blog/post-mortem-of-a-targeted-sodinokibi-ransomware-attack/
DoublePulsar LockerGoga | Kevin Beaumont. (n.d.). How Lockergoga took down Hydro — ransomware used in targeted attacks aimed at big business. Retrieved October 16, 2019. | https://doublepulsar.com/how-lockergoga-took-down-hydro-ransomware-used-in-targeted-attacks-aimed-at-big-business-c666551f5880
Dragos 2018 | Dragos Threat Intelligence. (2018). ICS Activity Groups and Threat Landscape. Retrieved January 3, 2020. | https://dragos.com/wp-content/uploads/yir-ics-activity-groups-threat-landscape-2018.pdf
Dragos Allanite | Dragos. (n.d.). Allanite. Retrieved October 27, 2019. | https://dragos.com/resource/allanite/
Dragos Apr 2019 | Joe Slowik. (2019, April 10). Implications of IT Ransomware for ICS Environments. Retrieved October 27, 2019. | https://dragos.com/blog/industry-news/implications-of-it-ransomware-for-ics-environments/
Dragos Aug 2019 | Dragos Threat Intelligence. (2019, August). Global Oil and Gas Cyber Threat Perspective. Retrieved January 3, 2020. | https://dragos.com/wp-content/uploads/Dragos-Oil-and-Gas-Threat-Perspective-2019.pdf
Dragos CRASHOVERRIDE | Dragos. (2018, October 12). Anatomy of an Attack: Detecting and Defeating CRASHOVERRIDE. Retrieved October 14, 2019. | https://dragos.com/wp-content/uploads/CRASHOVERRIDE2018.pdf
Dragos CRASHOVERRIDE Aug 2019 | Joe Slowik. (2019, August 15). CRASHOVERRIDE: Reassessing the 2016 Ukraine Electric Power Event as a Protection-Focused Attack. Retrieved October 22, 2019. | https://dragos.com/wp-content/uploads/CRASHOVERRIDE.pdf
Dragos CRASHOVERRIDE Oct 2018 | Dragos. (2018, October 12). Anatomy of an Attack: Detecting and Defeating CRASHOVERRIDE. Retrieved October 14, 2019. | https://dragos.com/wp-content/uploads/CRASHOVERRIDE2018.pdf
Dragos CRASHOVERRIDE October 2018 | Dragos. (2018, October 12). Anatomy of an Attack: Detecting and Defeating CRASHOVERRIDE. Retrieved October 14, 2019. | https://dragos.com/wp-content/uploads/CRASHOVERRIDE2018.pdf
Dragos EKANS February 2020 | Dragos Threat Intelligence. (2020, February 03). EKANS Ransomware and ICS Operations. Retrieved April 12, 2021. | https://www.dragos.com/blog/industry-news/ekans-ransomware-and-ics-operations/
Dragos Electrum | Dragos. (n.d.). Electrum. Retrieved October 27, 2019. | https://dragos.com/resource/electrum/
Dragos Hexane | Dragos. (n.d.). Hexane. Retrieved October 27, 2019. | https://dragos.com/resource/hexane/
Dragos Industroyer Jun 2017 | Dragos Inc.. (2017, June 13). Industroyer - Dragos - 201706: Analysis of the Threat to Electic Grid Operations. Retrieved September 18, 2017. | https://dragos.com/blog/crashoverride/CrashOverride-01.pdf
Dragos Magnallium | Dragos. (n.d.). Magnallium. Retrieved October 27, 2019. | https://dragos.com/resource/magnallium/
Dragos Mar 2018 | Eduard Kovacs. (2018, March 1). Five Threat Groups Target Industrial Systems: Dragos. Retrieved January 3, 2020. | https://www.securityweek.com/five-threat-groups-target-industrial-systems-dragos
Dragos Ransomware in ICS Environments Dec 2020 | Selena Larson, Camille Singleton. (2020, December). RANSOMWARE IN ICS ENVIRONMENTS. Retrieved April 12, 2021. | https://f.hubspotusercontent10.net/hubfs/5943619/Whitepaper-Downloads/Ransomware_in_ICS_Environments_Whitepaper_10_12_20.pdf?utm_referrer=https%3A%2F%2Fwww.dragos.com%2Fresource%2Fransomware-in-ics-environments%2F
Dragos Sept 2018 | Dragos Threat Intelligence. (2018, September 17). THREAT INTELLIGENCE SUMMARY TR-2018-25: Phishing Campaign Targeting Electric Utility Companies. Retrieved January 3, 2020. | https://dragos.com/wp-content/uploads/Sample-WorldView-Report.pdf
Dragos TRISIS Dec 2017 | Dragos. (2017, December 13). TRISIS Malware Analysis of Safety System Targeted Malware. Retrieved January 12, 2018. | https://dragos.com/blog/trisis/TRISIS-01.pdf
E-ISAC Allanite May 2018 | Jeff Jones. (2018, May 10). Dragos Releases Details on Suspected Russian Infrastructure Hacking Team ALLANITE. Retrieved January 3, 2020. | https://www.eisac.com/public-news-detail?id=115909
ESET Bad Rabbit Oct 2017 | Marc-Etienne M.Léveillé. (2017, October 24). Bad Rabbit: Not‑Petya is back with improved ransomware. Retrieved October 27, 2019. | https://www.welivesecurity.com/2017/10/24/bad-rabbit-not-petya-back/
ESET BlackEnergy | Anton Cherepanov. (n.d.). BlackEnergy by the SSHBearDoor: attacks against Ukrainian news media and electric industry. Retrieved October 29, 2019. | https://www.welivesecurity.com/2016/01/03/blackenergy-sshbeardoor-details-2015-attacks-ukrainian-news-media-electric-industry/
ESET Win32/Industroyer Jun 2017 | Anton Cherepanov, ESET. (2017, June 12). Win32/Industroyer: A new threat for industrial control systems. Retrieved September 15, 2017. | https://www.welivesecurity.com/wp-content/uploads/2017/06/Win32_Industroyer.pdf
ESET Win32/Industroyer June 2017 | Anton Cherepanov, ESET. (2017, June 12). Win32/Industroyer: A new threat for industrial control systems. Retrieved September 15, 2017. | https://www.welivesecurity.com/wp-content/uploads/2017/06/Win32_Industroyer.pdf
F-Secure Havex June 2014 | Daavid Hentunen, Antti Tikkanen. (2014, June 23). Havex Hunts For ICS/SCADA Systems. Retrieved April 1, 2019. | https://www.f-secure.com/weblog/archives/00002718.html
F-Secure Labs Jun 2014 | Daavid Hentunen, Antti Tikkanen. (2014, June 23). Havex Hunts For ICS/SCADA Systems. Retrieved April 1, 2019. | https://www.f-secure.com/weblog/archives/00002718.html
FireEye APT33 Sept 2017 | O'Leary, J., et al. (2017, September 20). Insights into Iranian Cyber Espionage: APT33 Targets Aerospace and Energy Sectors and has Ties to Destructive Malware. Retrieved February 15, 2018. | https://www.fireeye.com/blog/threat-research/2017/09/apt33-insights-into-iranian-cyber-espionage.html
FireEye Havex Jul 2014 | Kyle Wilhoit. (2014, July 17). Havex, It’s Down With OPC. Retrieved October 22, 2019. | https://www.fireeye.com/blog/threat-research/2014/07/havex-its-down-with-opc.html
FireEye OT Ransomware July 2020 | Nathan Brubaker, Daniel Kapellmann Zafra, Keith Lunden, Ken Proska, Corey Hildebrandt. (2020, July 15). Financially Motivated Actors Are Expanding Access Into OT: Analysis of Kill Lists That Include OT Processes Used With Seven Malware Families. Retrieved April 12, 2021. | https://www.fireeye.com/blog/threat-research/2020/07/financially-motivated-actors-are-expanding-access-into-ot.html
FireEye Ransomware Against the Machine July 2020 | Daniel Kapellmann Zafra, Keith Lunden, Nathan Brubaker, Jeremy Kennelly. (2020, July 15). Ransomware Against the Machine: How Adversaries are Learning to Disrupt Industrial Production by Targeting IT and OT. Retrieved April 12, 2021. | https://www.fireeye.com/blog/threat-research/2020/02/ransomware-against-machine-learning-to-disrupt-industrial-production.html
FireEye TRITON Dec 2017 | Blake Johnson, Dan Caban, Marina Krotofil, Dan Scali, Nathan Brubaker, Christopher Glyer. (2017, December 14). Attackers Deploy New ICS Attack Framework “TRITON” and Cause Operational Disruption to Critical Infrastructure. Retrieved January 12, 2018. | https://www.fireeye.com/blog/threat-research/2017/12/attackers-deploy-new-ics-attack-framework-triton.html
Forbes Snake Ransomware June 2020 | Davey Winder. (2020, June 10). Honda Hacked: Japanese Car Giant Confirms Cyber Attack On Global Operations. Retrieved April 12, 2021. | https://www.forbes.com/sites/daveywinder/2020/06/10/honda-hacked-japanese-car-giant-confirms-cyber-attack-on-global-operations-snake-ransomware/?sh=2725c35753ad
Fortinet EKANS July 2020 | Ben Hunter and Fred Gutierrez. (2020, July 01). EKANS Ransomware Targeting OT ICS Systems. Retrieved April 12, 2021. | https://www.fortinet.com/blog/threat-research/ekans-ransomware-targeting-ot-ics-systems
Hydro | Hydro. (n.d.). Retrieved October 16, 2019. | https://www.hydro.com/en/media/on-the-agenda/cyber-attack/
ICS Malware: Havex and Black Energy | Kyle Wilhoit. (n.d.). ICS Malware: Havex and Black Energy. Retrieved October 22, 2019. | https://www.youtube.com/watch?v=eywmb7UDODY&feature=youtu.be&t=939
ICS SANS Ukraine March 2018 | Electricity Information Sharing and Analysis Center; SANS Industrial Control Systems. (2016, March 18). Analysis of the Cyber Attack on the Ukranian Power Grid: Defense Use Case. Retrieved March 27, 2018. | https://ics.sans.org/media/E-ISAC_SANS_Ukraine_DUC_5.pdf
ICS-CERT Advantech/Broadwin WebAccess RPC Vulnerability September 2018 | ICS CERT. (2018, September 06). Advantech/Broadwin WebAccess RPC Vulnerability (Update B). Retrieved December 5, 2019. | https://www.us-cert.gov/ics/advisories/ICSA-11-094-02B
ICS-CERT ICS-Alert-14-281-01E December 2014 | ICS-CERT. (2014, December 10). ICS Alert (ICS-ALERT-14-281-01E) Ongoing Sophisticated Malware Campaign Compromising ICS (Update E). Retrieved October 11, 2019. | https://www.us-cert.gov/ics/alerts/ICS-ALERT-14-281-01B
ICS-CERT ICSA-14-178-01 August 2018 | ICS-CERT. (2018, August 22). Advisory (ICSA-14-178-01). Retrieved April 1, 2019. | https://ics-cert.us-cert.gov/advisories/ICSA-14-178-01
Kaspersky Bad Rabbit Oct 2017 | Orkhan Mamedov, Fedor Sinitsyn, Anton Ivanov. (2017, October 27). Bad Rabbit Ransomware. Retrieved October 27, 2019. | https://securelist.com/bad-rabbit-ransomware/82851/
Langner Nov 2013 | Ralph Langner. (2013, November). To Kill a Centrifuge: A Technical Analysis of What Stuxnet's Creators Tried to Achieve. Retrieved March 27, 2018. | https://www.langner.com/wp-content/uploads/2017/03/to-kill-a-centrifuge.pdf
MDudek-ICS TRISIS-TRITON-HATMAN | MDudek-ICS. (n.d.). TRISIS-TRITON-HATMAN. Retrieved November 3, 2019. | https://github.com/MDudek-ICS/TRISIS-TRITON-HATMAN/tree/master/decompiled_code/library
MITRE CVE-2018-8872 May 2018 | MITRE. (2018, May 04). CVE-2018-8872. Retrieved March 8, 2019. | https://nvd.nist.gov/vuln/detail/CVE-2018-8872
McAfee Sodinokibi October 2019 | McAfee Labs. (2019, October 02). McAfee ATR Analyzes Sodinokibi aka REvil Ransomware-as-a-Service – What The Code Tells Us. Retrieved April 12, 2021. | https://www.mcafee.com/blogs/other-blogs/mcafee-labs/mcafee-atr-analyzes-sodinokibi-aka-revil-ransomware-as-a-service-what-the-code-tells-us
Midnight Blue Labs TRITON Jan 2018 | Jos Wetzels. (2018, January 16). Analyzing the TRITON industrial malware. Retrieved October 22, 2019. | https://www.midnightbluelabs.com/blog/2018/1/16/analyzing-the-triton-industrial-malware
Midnight Blue Labs Triton January 2018 | Jos Wetzels. (2018, January 16). Analyzing the TRITON industrial malware. Retrieved October 22, 2019. | https://www.midnightbluelabs.com/blog/2018/1/16/analyzing-the-triton-industrial-malware
NRC Triconex | The Office of Nuclear Reactor Regulation. (n.d.). Triconex Topical Report 7286-545-1. Retrieved May 30, 2018. | https://www.nrc.gov/docs/ML1209/ML120900890.pdf
Novetta Blockbuster | Novetta Threat Research Group. (2016, February 24). Operation Blockbuster: Unraveling the Long Thread of the Sony Attack. Retrieved February 25, 2016. | https://www.operationblockbuster.com/wp-content/uploads/2016/02/Operation-Blockbuster-Report.pdf
PaloAlto OilRig May 2016 | Robert Falcone, Bryan Lee. (2016, May 26). The OilRig Campaign: Attacks on Saudi Arabian Organizations Deliver Helminth Backdoor. Retrieved November 19, 2019. | https://unit42.paloaltonetworks.com/the-oilrig-campaign-attacks-on-saudi-arabian-organizations-deliver-helminth-backdoor/
Schneider Electric TRITON Jan 2018 | Schneider Electric. (2018, January 23). TRITON - Schneider Electric Analysis and Disclosure. Retrieved March 14, 2019. | https://www.youtube.com/watch?v=f09E75bWvkk&index=3&list=PL8OWO1qWXF4qYG19p7An4Vw3N2YZ86aRS&t=0s
SecureWorks LYCEUM Aug 2019 | SecureWorks. (2019, August 27). LYCEUM Takes Center Stage in Middle East Campaign. Retrieved November 19, 2019. | https://www.secureworks.com/blog/lyceum-takes-center-stage-in-middle-east-campaign
SecureWorks REvil/Sodinokibi 2019 | SecureWorks. (2019, September 24). REvil/Sodinokibi Ransomware. Retrieved April 12, 2021. | https://www.secureworks.com/research/revil-sodinokibi-ransomware
SecurityWeek Allanite May 2018 | Eduard Kovacs. (2018, May 10). 'Allanite' Group Targets ICS Networks at Electric Utilities in US, UK. Retrieved January 3, 2020. | https://www.securityweek.com/allanite-group-targets-ics-networks-electric-utilities-us-uk
SecurityWeek Hexane Aug 2019 | Ionut Arghire. (2019, August 28). Researchers Analyze Tools Used by 'Hexane' Attackers Against Industrial Firms. Retrieved January 3, 2020. | https://www.securityweek.com/researchers-analyze-tools-used-hexane-attackers-against-industrial-firms
SemanticScholar Dec 2015 | Julian Rrushi, Hassan Farhangi, Clay Howey, Kelly Carmichael, Joey Dabell. (2015, December 08). A Quantitative Evaluation of the Target Selection of Havex ICS Malware Plugin. Retrieved April 1, 2019. | https://pdfs.semanticscholar.org/18df/43ef1690b0fae15a36f770001160aefbc6c5.pdf
Softpedia News Apr 2016 | Catalin Cimpanu. (2016, April 26). Malware Shuts Down German Nuclear Power Plant on Chernobyl's 30th Anniversary. Retrieved October 14, 2019. | https://news.softpedia.com/news/on-chernobyl-s-30th-anniversary-malware-shuts-down-german-nuclear-power-plant-503429.shtml
Symantec Conficker Jun 20 | Symantec. (2015, June 30). Simple steps to protect yourself from the Conficker Worm. Retrieved December 5, 2019. | https://support.symantec.com/us/en/article.tech93179.html
Symantec Dragonfly Sept 2017 | Symantec. (2017, September 6). Dragonfly: Western energy sector targeted by sophisticated attack group. Retrieved September 14, 2017. | https://www.symantec.com/connect/blogs/dragonfly-western-energy-sector-targeted-sophisticated-attack-group
Symantec Elfin Mar 2019 | Symantec. (2019, March 27). Elfin: Relentless Espionage Group Targets Multiple Organizations in Saudi Arabia and U.S.. Retrieved December 2, 2019. | https://www.symantec.com/blogs/threat-intelligence/elfin-apt33-espionage
Symantec Trojan.Stonedrill Mar 2017 | Junnosuke Yagi. (2017, March 07). Trojan.Stonedrill. Retrieved December 5, 2019. | https://www.symantec.com/security-center/writeup/2017-030708-4403-99
Symantec W.32 Duqu | Symantec. (n.d.). W32.Duqu The precursor to the next Stuxnet. Retrieved November 3, 2019. | https://www.symantec.com/content/en/us/enterprise/media/security_response/whitepapers/w32_duqu_the_precursor_to_the_next_stuxnet.pdf
Symantec W32.Flamer | Kevin Savage and Branko Spasojevic. (n.d.). W32.Flamer. Retrieved November 3, 2019. | https://www.symantec.com/security-center/writeup/2012-052811-0308-99
Talos Jul 2017 | Sean Baird, Earl Carter, Erick Galinkin, Christopher Marczewski & Joe Marshall. (2017, July 07). Attack on Critical Infrastructure Leverages Template Injection. Retrieved December 5, 2019. | https://blog.talosintelligence.com/2017/07/template-injection.html
Talos VPNFilter Jun 2018 | William Largent. (2018, June 06). VPNFilter Update - VPNFilter exploits endpoints, targets new devices. Retrieved March 28, 2019. | https://blog.talosintelligence.com/2018/06/vpnfilter-update.html
VPNFilter Deep Dive Mar 2019 | Carl Hurd. (2019, March 26). VPNFilter Deep Dive. Retrieved March 28, 2019. | https://www.youtube.com/watch?v=yuZazP22rpI
Wired Jun 2019 | Andy Greenburg. (2019, June 20). Iranian Hackers Launch a New US-Targeted Campaign as Tensions Mount. Retrieved January 3, 2020. | https://www.wired.com/story/iran-hackers-us-phishing-tensions/
Wired W32.Stuxnet Feb 2011 | Nicolas Falliere, Liam O Murchu, Eric Chien. (2011, February). W32.Stuxnet Dossier (Version 1.4). Retrieved September 22, 2017. | https://www.wired.com/images_blogs/threatlevel/2010/11/w32_stuxnet_dossier.pdf
Maroochy - MITRE - 200808 | Marshall Abrams. (2008, July 23). Malicious Control System Cyber Security Attack Case Study– Maroochy Water Services, Australia. Retrieved March 27, 2018. | https://www.mitre.org/sites/default/files/pdf/08%201145.pdf
References - Secura - 2019 | Jos Wetzels, Marina Krotofil. (2019). A Diet of Poisoned Fruit: Designing Implants & OT Payloads for ICS Embedded Devices. Retrieved November 1, 2019. | https://troopers.de/downloads/troopers19/TROOPERS19%20NGI%20IoT%20diet%20poisoned%20fruit.pdf
Research - Research - Taxonomy Cyber Attacks on SCADA | Bonnie Zhu, Anthony Joseph, Shankar Sastry. (2011). A Taxonomy of Cyber Attacks on SCADA Systems. Retrieved January 12, 2018. | http://ieeexplore.ieee.org/stamp/stamp.jsp?tp=&arnumber=6142258
Ukraine15 - EISAC - 201603 | Electricity Information Sharing and Analysis Center; SANS Industrial Control Systems. (2016, March 18). Analysis of the Cyber Attack on the Ukranian Power Grid: Defense Use Case. Retrieved March 27, 2018. | https://ics.sans.org/media/E-ISAC%20SANS%20Ukraine%20DUC%205.pdf
Forum Automation PLC Operating Modes October 2017 | N.A.. (2017, October). What are the different operating modes in PLC?. Retrieved January 28, 2021. | https://forumautomation.com/t/what-are-the-different-operating-modes-in-plc/2489
Omrom PLC Different Operating Modes | Omron. (n.d.). PLC Different Operating Modes. Retrieved January 28, 2021. | https://www.omron-ap.com/service_support/FAQ/FAQ00002/index.asp#:~:text=In%20PROGRAM%20mode%2C%20the%20CPU,can%20be%20created%20or%20modified.
Machine Information Systems How PLCs Work 2007 | Machine Information Systems. (2007). How PLCs Work. Retrieved January 28, 2021. | http://www.machine-information-systems.com/How_PLCs_Work.html
PLCgurus PLC Basics 2021 | PLCgurus. (2021). PLC Basics – Modes Of Operation. Retrieved January 28, 2021. | https://www.plcgurus.net/plc-basics/
EAttack Command-Line Interface | Enterprise ATT&CK. (2018, January 11). Command-Line Interface. Retrieved May 17, 2018. | https://attack.mitre.org/wiki/Technique/T1059
EAttack Connection Proxy | Enterprise ATT&CK. (2018, January 11). Connection Proxy. Retrieved May 17, 2018. | https://attack.mitre.org/wiki/Technique/T1090
University of Birmingham C2 | Gardiner, J., Cova, M., Nagaraja, S. (2014, February). Command & Control Understanding, Denying and Detecting. Retrieved April 20, 2016. | https://www.cpni.gov.uk/Documents/Publications/2014/2014-04-23-c2-report-birmingham.pdf
LodzTram-LondonReconnections-2017-12 | John Bill. (2017, May 12). Hacked Cyber Security Railways. Retrieved October 17, 2019. | https://www.londonreconnections.com/2017/hacked-cyber-security-railways/
LodzTram-InHomelandSecurity-2008-02 | Shelley Smith. (2008, February 12). Teen Hacker in Poland Plays Trains and Derails City Tram System. Retrieved October 17, 2019. | https://inhomelandsecurity.com/teen%20hacker%20in%20poland%20plays%20tr/
LodzTram-Schneier-2008-01 | Bruce Schneier. (2008, January 17). Hacking Polish Trams. Retrieved October 17, 2019. | https://www.schneier.com/blog/archives/2008/01/hacking%20the%20pol.html
German Steel Mill - German Federal Office for Information Security - 2014 | Bundesamt für Sicherheit in der Informationstechnik (BSI) (German Federal Office for Information Security). (2014). Die Lage der IT-Sicherheit in Deutschland 2014 (The State of IT Security in Germany). Retrieved October 30, 2019. | https://www.bsi.bund.de/SharedDocs/Downloads/EN/BSI/Publications/Securitysituation/IT-Security-Situation-in-Germany-2014.pdf?%20blob=publicationFile&v=3
EAttack File Deletion | Enterprise ATT&CK. (2018, January 11). File Deletion. Retrieved May 17, 2018. | https://attack.mitre.org/wiki/Technique/T1107
CISA Chinese Gas Pipeline Intrusion 2011 - 2013 July 2021 | ONG2011 - DHS Advisory - Department of Justice (DOJ), DHS Cybersecurity & Infrastructure Security Agency (CISA). (2021, July 20). Chinese Gas Pipeline Intrusion Campaign, 2011 to 2013. Retrieved October 8, 2021. | https://us-cert.cisa.gov/sites/default/files/publications/AA21-201A_Chinese_Gas_Pipeline_Intrusion_Campaign_2011_to_2013%20(1).pdf
Guidance - NIST SP800-82 | Keith Stouffer. (2015, May). Guide to Industrial Control Systems (ICS) Security. Retrieved March 28, 2018. | https://nvlpubs.nist.gov/nistpubs/SpecialPublications/NIST.SP.800-82r2.pdf
Reference - Corero | Corero. (n.d.). Industrial Control System (ICS) Security. Retrieved November 4, 2019. | https://www.corero.com/resources/files/whitepapers/cns%20whitepaper%20ics.pdf
Reference - SANS - 201510 | Michael J. Assante and Robert M. Lee. (n.d.). The Industrial Control System Cyber Kill Chain. Retrieved November 4, 2019. | https://www.sans.org/reading-room/whitepapers/ICS/industrial-control-system-cyber-kill-chain-36297
Reference - RIoT | Tyson Macaulay. (n.d.). RIoT Control: Understanding and Managing Risks and the Internet of Things. Retrieved November 4, 2019.
BrickerBot - ICS-CERT - Alert | ICS-CERT. (2017, April 18). CS Alert (ICS-ALERT-17-102-01A) BrickerBot Permanent Denial-of-Service Attack. Retrieved October 24, 2019. | https://www.us-cert.gov/ics/alerts/ICS-ALERT-17-102-01A
Industroyer - ICS-CERT ADV | ICS-CERT. (2018, August 27). Advisory (ICSA-15-202-01) - Siemens SIPROTEC Denial-of-Service Vulnerability. Retrieved March 14, 2019. | https://ics-cert.us-cert.gov/advisories/ICSA-15-202-01
Industroyer - CWE-400 | Common Weakness Enumeration. (2019, January 03). CWE-400: Uncontrolled Resource Consumption. Retrieved March 14, 2019. | http://cwe.mitre.org/data/definitions/400.html
Industroyer - CVE-2015-5374 | MITRE. (2018, March 22). CVE-2015-5374. Retrieved March 14, 2019. | https://nvd.nist.gov/vuln/detail/CVE-2015-5374
ForumAutomation PLC Operating Modes October 2017 | N.A.. (2017, October). What are the different operating modes in PLC?. Retrieved January 28, 2021. | https://forumautomation.com/t/what-are-the-different-operating-modes-in-plc/2489
Omron PLC Operating Modes | Omron. (n.d.). PLC Different Operating Modes. Retrieved January 28, 2021. | https://www.omron-ap.com/service_support/FAQ/FAQ00002/index.asp#:~:text=In%20PROGRAM%20mode%2C%20the%20CPU,can%20be%20created%20or%20modified.
Machine Information Systems PLCs 2007 | Machine Information Systems. (2007). How PLCs Work. Retrieved January 28, 2021. | http://www.machine-information-systems.com/How_PLCs_Work.html
PLCgurus PLC Basic 2021 | PLCgurus. (2021). PLC Basics – Modes Of Operation. Retrieved January 28, 2021. | https://www.plcgurus.net/plc-basics/
Alert - CISA TA18-074A | NCAS. (2018, March 15). Alert (TA18-074A) Russian Government Cyber Activity Targeting Energy and Other Critical Infrastructure Sectors. Retrieved October 11, 2019. | https://www.us-cert.gov/ncas/alerts/TA18-074A
ICS CERT 14-281 | ICS-CERT. (2014, December 10). ICS Alert (ICS-ALERT-14-281-01E) Ongoing Sophisticated Malware Campaign Compromising ICS (Update E). Retrieved October 11, 2019. | https://www.us-cert.gov/ics/alerts/ICS-ALERT-14-281-01B
ATT&CK Exploitation for Privilege Escalation | The MITRE Corporation. (n.d.). ATT&CK T1068: Exploitation for Privilege Escalation. Retrieved April 12, 2021. | https://attack.mitre.org/techniques/T1068/
EAttack Exploitation of Remote Services | Enterprise ATT&CK. (n.d.). Exploitation of Remote Services. Retrieved October 27, 2019. | https://attack.mitre.org/techniques/T1210/
Reference - Dragos - 201910 | Joe Slowik. (2019, April 10). Implications of IT Ransomware for ICS Environments. Retrieved October 27, 2019. | https://dragos.com/blog/industry-news/implications-of-it-ransomware-for-ics-environments/
EAttack External Remote Services | Daniel Oakley, Travis Smith, Tripwire. (n.d.). Retrieved May 30, 2018. | https://attack.mitre.org/wiki/Technique/T1133
Ukraine15 - Zetter, Kim | Zetter, Kim. (2016, March 03). INSIDE THE CUNNING, UNPRECEDENTED HACK OF UKRAINE'S POWER GRID. Retrieved March 8, 2019. | https://www.wired.com/2016/03/inside-cunning-unprecedented-hack-ukraines-power-grid/
Ukraine15 - ICSCERT | ICS-CERT. (2016, February 25). Cyber-Attack Against Ukrainian Critical Infrastructure. Retrieved March 8, 2019. | https://ics-cert.us-cert.gov/alerts/IR-ALERT-H-16-056-01
Ukraine15 - Fireeye | John Hultquist. (2016, January 07). Sandworm Team and the Ukrainian Power Authority Attacks. Retrieved March 8, 2019. | https://www.fireeye.com/blog/threat-research/2016/01/ukraine-and-sandworm-team.html
Oldsmar Water Treatment Attack Feb 2021 | Pinellas County Sheriff’s Office. (2021, February 8). Treatment Plant Intrusion Press Conference. Retrieved October 8, 2021. | https://www.youtube.com/watch?v=MkXDSOgLQ6M
EAttack Hooking | Enterprise ATT&CK. (n.d.). Hooking. Retrieved October 27, 2019. | https://attack.mitre.org/techniques/T1179/
Stuxnet - Symantec - 201102 | Nicolas Falliere, Liam O Murchu, Eric Chien. (2011, February). W32.Stuxnet Dossier (Version 1.4). Retrieved September 22, 2017. | https://www.symantec.com/content/en/us/enterprise/media/security%20response/whitepapers/w32%20stuxnet%20dossier.pdf
PLC-Blaster 2 | Spenneberg, Ralf. (2016). PLC-Blaster. Retrieved June 6, 2019. | https://www.blackhat.com/docs/asia-16/materials/asia-16-Spenneberg-PLC-Blaster-A-Worm-Living-Solely-In-The-PLC.pdf
Bowman Dam - ICS-CERT | NCCIC. (2014, January 1). Internet Accessible Control Systems At Risk. Retrieved November 7, 2019. | https://www.us-cert.gov/sites/default/files/Monitors/ICS-CERT%20Monitor%20Jan-April2014.pdf
Bowman Dam - wall street journal | Danny Yadron. (2015, December 20). Iranian Hackers Infiltrated New York Dam in 2013. Retrieved November 7, 2019. | https://www.wsj.com/articles/iranian-hackers-infiltrated-new-york-dam-in-2013-1450662559
Bowman Dam - Times | Mark Thompson. (2016, March 24). Iranian Cyber Attack on New York Dam Shows Future of War. Retrieved November 7, 2019. | https://time.com/4270728/iran-cyber-attack-dam-fbi/
Trend Micro Honeypot | Stephen Hilt, Federico Maggi, Charles Perine, Lord Remorin, Martin Rösler, and Rainer Vosseler. (n.d.). Caught in the Act: Running a Realistic Factory Honeypot to Capture Real Threats. Retrieved April 12, 2021. | https://documents.trendmicro.com/assets/white_papers/wp-caught-in-the-act-running-a-realistic-factory-honeypot-to-capture-real-threats.pdf
EAttack Lateral Tool Transfer | Enterprise ATT&CK. (n.d.). Lateral Tool Transfer. Retrieved October 27, 2019. | https://attack.mitre.org/techniques/T1570/
BSI IT Security Situation 2014 | Bundesamt für Sicherheit in der Informationstechnik (BSI) (German Federal Office for Information Security). (2014). Die Lage der IT-Sicherheit in Deutschland 2014 (The State of IT Security in Germany). Retrieved October 30, 2019. | https://www.bsi.bund.de/SharedDocs/Downloads/EN/BSI/Publications/Securitysituation/IT-Security-Situation-in-Germany-2014.pdf?__blob=publicationFile&v=3
Distrupted Operations at Lion Company June 2020 | Paganini, Pierluigi. (2020, June 14). Ransomware attack disrupts operations at Australian beverage company Lion. Retrieved October 8, 2021. | https://securityaffairs.co/wordpress/104749/cyber-crime/ransomware-attack-hit-lion.html
Lion Cyber Incident June 2020 | Lion Corporation. (2020, June 26). Lion Cyber incident update: 26 June 2020. Retrieved October 8, 2021. | https://lionco.com/2020/06/26/lion-update-re-cyber-issue/
Colonial Pipeline System Distruption May 2021 | Colonial Pipeline Company. (2021, May). Media Statement Update: Colonial Pipeline System Disruption. Retrieved October 8, 2021. | https://www.colpipe.com/news/press-releases/media-statement-colonial-pipeline-system-disruption
Reference - SANS - 201710 | Gabriel Sanchez. (2017, October). Man-In-The-Middle Attack Against Modbus TCP Illustrated with Wireshark. Retrieved January 5, 2020. | https://www.sans.org/reading-room/whitepapers/ICS/man-in-the-middle-attack-modbus-tcp-illustrated-wireshark-38095
Guidance - ISA PLC | Dr. Kelvin T. Erickson. (2010, December). Programmable logic controller hardware. Retrieved March 29, 2018. | https://www.isa.org/standards-and-publications/isa-publications/intech/2010/december/programmable-logic-controller-hardware/
LondonReconnections Hacked Cyber Security Railways May 2017 | John Bill. (2017, May 12). Hacked Cyber Security Railways. Retrieved October 17, 2019. | https://www.londonreconnections.com/2017/hacked-cyber-security-railways/
InHomelandSecurity Hacker Poland February 2008 | Shelley Smith. (2008, February 12). Teen Hacker in Poland Plays Trains and Derails City Tram System. Retrieved October 17, 2019. | https://inhomelandsecurity.com/teen_hacker_in_poland_plays_tr/
Schneier Hacking Polish Trams January 2008 | Bruce Schneier. (2008, January 17). Hacking Polish Trams. Retrieved October 17, 2019. | https://www.schneier.com/blog/archives/2008/01/hacking_the_pol.html
IEC Programmable controllers February 2013 | IEC. (2013, February 20). IEC 61131-3:2013 Programmable controllers - Part 3: Programming languages. Retrieved October 22, 2019. | https://webstore.iec.ch/publication/4552
References - Module Firmware | Daniel Peck, Dale Peterson. (2009, January 28). Leveraging Ethernet Card Vulnerabilities in Field Devices. Retrieved December 19, 2017. | https://www.researchgate.net/publication/228849043%20Leveraging%20ethernet%20card%20vulnerabilities%20in%20field%20devices
EAttack Native API | The MITRE Corporation. (2017, May 31). ATT&CK T1106: Native API. Retrieved April 26, 2021. | https://attack.mitre.org/techniques/T1106/
EAttack System Network Connections Discovery | MITRE. (n.d.). System Network Connections Discovery. Retrieved May 31, 2018. | https://attack.mitre.org/wiki/Technique/T1049
EAttack Network Sniffing | Enterprise ATT&CK. (2018, January 11). Network Sniffing. Retrieved May 17, 2018. | https://attack.mitre.org/wiki/Technique/T1040
References - tags process comprehension | Benjamin Green. (n.d.). On the Significance of Process Comprehension for Conducting Targeted ICS Attacks. Retrieved November 1, 2019. | http://www.research.lancs.ac.uk/portal/files/196578358/sample%20sigconf.pdf
References - beckhoff project files | Beckhoff. (n.d.). TwinCAT 3 Source Control: Project Files. Retrieved November 21, 2019. | https://infosys.beckhoff.com/english.php?content=../content/1033/tc3%20sourcecontrol/18014398915785483.html&id=
References - plcdev siemens | PLCdev. (n.d.). Siemens SIMATIC Step 7 Programmer's Handbook. Retrieved November 21, 2019. | http://www.plcdev.com/book/export/html/373
FireEye TRITON December 2017 | Blake Johnson, Dan Caban, Marina Krotofil, Dan Scali, Nathan Brubaker, Christopher Glyer. (2017, December 14). Attackers Deploy New ICS Attack Framework “TRITON” and Cause Operational Disruption to Critical Infrastructure. Retrieved January 12, 2018. | https://www.fireeye.com/blog/threat-research/2017/12/attackers-deploy-new-ics-attack-framework-triton.html
Dragos TRISIS December 2017 | Dragos. (2017, December 13). TRISIS Malware Analysis of Safety System Targeted Malware. Retrieved January 12, 2018. | https://dragos.com/blog/trisis/TRISIS-01.pdf
Dragos IT ICS Ransomware December April 2019 | Joe Slowik. (2019, April 10). Implications of IT Ransomware for ICS Environments. Retrieved October 27, 2019. | https://dragos.com/blog/industry-news/implications-of-it-ransomware-for-ics-environments/
EAttack Remote System Discovery | Enterprise ATT&CK. (2018, January 11). Remote System Discovery. Retrieved May 17, 2018. | https://attack.mitre.org/wiki/Technique/T1018
KGG-Company-Site | Kernkraftwerk Gundremmingen. (2016, April 25). Detektion von Büro-Schadsoftware an mehreren Rechnern. Retrieved October 14, 2019. | https://www.kkw-gundremmingen.de/presse.php?id=571
KGG-Softpedia | Catalin Cimpanu. (2016, April 26). Malware Shuts Down German Nuclear Power Plant on Chernobyl's 30th Anniversary. Retrieved October 14, 2019. | https://news.softpedia.com/news/on-chernobyl-s-30th-anniversary-malware-shuts-down-german-nuclear-power-plant-503429.shtml
KGG-Reuters | Christoph Steitz, Eric Auchard. (2016, April 26). German nuclear plant infected with computer viruses, operator says. Retrieved October 14, 2019. | https://www.reuters.com/article/us-nuclearpower-cyber-germany/german-nuclear-plant-infected-with-computer-viruses-operator-says-idUSKCN0XN2OS
KGG-Science-Alert | Peter Dockrill. (2016, April 28). Multiple Computer Viruses Have Been Discovered in This German Nuclear Plant. Retrieved October 14, 2019. | https://www.sciencealert.com/multiple-computer-viruses-have-been-discovered-in-this-german-nuclear-plant
KGG-ESET | ESET. (2016, April 28). Malware found at a German nuclear power plant. Retrieved October 14, 2019. | https://www.welivesecurity.com/2016/04/28/malware-found-german-nuclear-power-plant/
KGG-Geek | Lee Mathews. (2016, April 27). German nuclear plant found riddled with Conficker, other viruses. Retrieved October 14, 2019. | https://www.geek.com/apps/german-nuclear-plant-found-riddled-with-conficker-other-viruses-1653415/
KGG-Trend Micro | Trend Micro. (2016, April 27). Malware Discovered in German Nuclear Power Plant. Retrieved October 14, 2019. | https://www.trendmicro.com/vinfo/us/security/news/cyber-attacks/malware-discovered-in-german-nuclear-power-plant
KGG-BBC | BBC. (2016, April 28). German nuclear plant hit by computer viruses. Retrieved October 14, 2019. | https://www.bbc.com/news/technology-36158606
KGG-Ars | Sean Gallagher. (2016, April 27). German nuclear plant’s fuel rod system swarming with old malware. Retrieved October 14, 2019. | https://arstechnica.com/information-technology/2016/04/german-nuclear-plants-fuel-rod-system-swarming-with-old-malware/
KGG-Dark | Dark Reading Staff. (2016, April 28). German Nuclear Power Plant Infected With Malware. Retrieved October 14, 2019. | https://www.darkreading.com/endpoint/german-nuclear-power-plant-infected-with-malware/d/d-id/1325298
EAttack Rootkit | Enterprise ATT&CK. (2018, January 11). Rootkit. Retrieved May 16, 2018. | https://attack.mitre.org/wiki/Technique/T1014
Alert - Russian APT TA18-074A - 201803 | ICS-CERT. (2017, October 21). Advanced Persistent Threat Activity Targeting Energy and Other Critical Infrastructure Sectors. Retrieved October 23, 2017. | https://www.us-cert.gov/ncas/alerts/TA17-293A
EAttack Service Stop | Enterprise ATT&CK. (n.d.). Service Stop. Retrieved October 29, 2019. | https://attack.mitre.org/techniques/T1489/
EAttack Spearphishing Attachment | Enterprise ATT&CK. (2019, October 25). Spearphishing Attachment. Retrieved October 25, 2019. | https://attack.mitre.org/techniques/T1193/
Control Global Yokogawa May 2019 | Control Global. (2019, May 29). Yokogawa announcement warns of counterfeit transmitters. Retrieved April 9, 2021. | https://www.controlglobal.com/industrynews/2019/yokogawa-announcement-warns-of-counterfeit-transmitters/
Havex - F-Secure - 201406 | F-Secure Labs. (2014, June 23). Havex Hunts For ICS/SCADA Systems. Retrieved October 21, 2019. | https://www.f-secure.com/weblog/archives/00002718.html
Havex - F-Secure | Daavid Hentunen, Antti Tikkanen. (2014, June 23). Havex Hunts For ICS/SCADA Systems. Retrieved April 1, 2019. | https://www.f-secure.com/weblog/archives/00002718.html
Research - Firmware Modification | Basnight, Zachry, et al.. (n.d.). Retrieved October 17, 2017. | http://www.sciencedirect.com/science/article/pii/S1874548213000231
StateScoop Dallas March 2019 | Benjamin Freed. (2019, March 13). Tornado sirens in Dallas suburbs deactivated after being hacked and set off. Retrieved November 6, 2020. | https://statescoop.com/tornado-sirens-in-dallas-suburbs-deactivated-after-being-hacked-and-set-off/
ZDNet Dallas April 2017 | Zack Whittaker. (2017, April 12). Dallas' emergency sirens were hacked with a rogue radio signal. Retrieved November 6, 2020. | https://www.zdnet.com/article/experts-think-they-know-how-dallas-emergency-sirens-were-hacked/
NERC June 2021 | North American Electric Reliability Corporation. (2021, June 28). Glossary of Terms Used in NERC Reliability Standards. Retrieved October 11, 2021. | https://www.nerc.com/files/glossary_of_terms.pdf
NIST Apr 2013 | National Institute of Standards and Technology. (2013, April). Security and Privacy Controls for Federal Information Systems and Organizations. Retrieved September 17, 2020. | https://nvlpubs.nist.gov/nistpubs/SpecialPublications/NIST.SP.800-53r4.pdf
NAFT Dec 2019 | North America Transmission Forum. (2019, December). NATF Transient Cyber Asset Guidance. Retrieved September 25, 2020. | https://www.natf.net/docs/natf/documents/resources/security/natf-transient-cyber-asset-guidance.pdf
Emerson Exchange | Emerson Exchange. (n.d.). Increase Security with TPM, Secure Boot, and Trusted Boot. Retrieved September 25, 2020. | https://emersonexchange365.com/products/control-safety-systems/f/plc-pac-systems-industrial-computing-forum/8383/increase-security-with-tpm-secure-boot-and-trusted-boot
National Security Agency Feb 2016 | National Security Agency. (2016, February). Position Zero: Integrity Checking Windows-Based ICS/SCADA Systems. Retrieved September 25, 2020. | https://apps.nsa.gov/iaarchive/library/ia-guidance/security-configuration/industrial-control-systems/position-zero-integrity-checking-windows-based-ics-scada-systems.cfm
BlackEnergy - Booz Allen Hamilton | Booz Allen Hamilton. (n.d.). When The Lights Went Out. Retrieved October 22, 2019. | https://www.boozallen.com/content/dam/boozallen/documents/2016/09/ukraine-report-when-the-lights-went-out.pdf
Hart - Bolshev | Alexander Bolshev. (2014, March 11). S4x14: HART As An Attack Vector. Retrieved January 5, 2020. | https://www.slideshare.net/dgpeters/17-bolshev-1-13
ICSCorsair - Bolshev | Alexander Bolshev, Gleb Cherbov. (2014, July 08). ICSCorsair: How I will PWN your ERP through 4-20 mA current loop. Retrieved January 5, 2020. | https://www.blackhat.com/docs/us-14/materials/us-14-Bolshev-ICSCorsair-How-I-Will-PWN-Your-ERP-Through-4-20mA-Current-Loop-WP.pdf
NIST AMS 300-4 April 2018 | Candell, R., Hany, M., Lee, K. B., Liu,Y., Quimby, J., Remley, K.. (2018, April). Guide to Industrial Wireless Systems Deployments. Retrieved December 1, 2020. | https://nvlpubs.nist.gov/nistpubs/ams/NIST.AMS.300-4.pdf
Bastille Dallas April 2017 | Bastille. (2017, April 17). Dallas Siren Attack. Retrieved November 6, 2020. | https://www.bastille.net/blogs/2017/4/17/dallas-siren-attack
Ars Technica Dallas April 2017 | Gallagher, S.. (2017, April 12). Pirate radio: Signal spoof set off Dallas emergency sirens, not network hack. Retrieved December 1, 2020. | https://arstechnica.com/information-technology/2017/04/dallas-siren-hack-used-radio-signals-to-spoof-alarm-says-city-manager/